## Turbidity Monitoring Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Yamhill
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-11-22
System Name: | City of Sheridan |  |  | ID#: 41 | 00811 |  | WTP : | WTP-A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | 0.06 | 0.3 | 0.15 | OFF | 0.48
2 | OFF | OFF | 0.12 | 0.25 | 0.17 | OFF | 0.57
3 | OFF | OFF | OFF | 0.22 | 0.2 | OFF | 0.61
4 | OFF | OFF | 0.14 | 0.14 | 0.24 | OFF | 0.34
5 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
6 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
7 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
8 | OFF | OFF | 0.22 | 0.18 | 0.22 | OFF | 0.27
9 | OFF | OFF | 0.1 | 0.4 | 0.15 | OFF | 0.6
10 | OFF | OFF | 0.09 | 0.09 | 0.08 | OFF | 0.15
11 | OFF | OFF | 0.06 | 0.2 | 0.17 | OFF | 0.39
12 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
13 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
14 | OFF | OFF | 0.14 | 0.17 | 0.17 | OFF | 0.49
15 | OFF | OFF | 0.21 | 0.16 | 0.08 | OFF | 0.17
16 | OFF | OFF | 0.25 | 0.1 | 0.15 | OFF | 0.28
17 | OFF | OFF | 0.06 | 0.2 | 0.13 | OFF | 0.24
18 | OFF | OFF | 0.11 | 0.1 | 0.14 | OFF | 0.32
19 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
20 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
21 | OFF | OFF | 0.11 | 0.32 | 0.31 | OFF | 0.6
22 | OFF | OFF | 0.16 | 0.29 | 0.2 | OFF | 0.38
23 | OFF | OFF | 0.22 | 0.07 | OFF | OFF | OFF
24 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
25 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
26 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
27 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
28 | OFF | OFF | 0.08 | 0.06 | 0.1 | OFF | 0.31
29 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
30 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | √ Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | √ Yes / No
All turbidity readings < IFE2 triggers |  |  |  | √ Yes / No | √ Yes / No |  | √ Yes / No
Notes: |  |  |  |  | PRINTED NAME: Gary N Mathis
[5 empty] | SIGNATURE: |  |  | DATE:12/9/2022
[5 empty] | PHONE #: (971) 312-1892 |  |  | CERT #:127558
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Surface Water Quality Data
| OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | WTP-A
System Name: |  | City of Sheridan |  | ID#: 41 00811 |  | Month/Year: | 2022-11-22 | Disinfection Giardia Log Inactiv: | 0.5
Date | Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
|  | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 8:00 | 1.86 | 65 | 120.9 | 16.2 | 7 | 13.8658 | Yes | 780
2 | 9:15 | 1.56 | 65 | 101.4 | 16.4 | 7 | 13.22 | Yes | 720
3 | 8:45 | 1.22 | 65 | 79.3 | 12.4 | 7.1 | 17.5252 | Yes | 720
4 | 11:20 | 1.48 | 65 | 96.2 | 13.6 | 7.1 | 16.3915 | Yes | 800
5 | 9:00 | 1.28 | 65 | 83.2 | 11.9 | 7 | 17.604 | Yes | 180
6 | 9:45 | 1.08 | 65 | 70.2 | 11.7 | 7 | 17.4438 | Yes | 110
7 | 9:55 | 0.98 | 65 | 63.7 | 12.5 | 7.2 | 17.29 | Yes | 440
8 | 10:00 | 1.2 | 65 | 78 | 12.5 | 7.2 | 17.7275 | Yes | 740
9 | 8:45 | 1.62 | 65 | 105.3 | 12.6 | 7.1 | 17.8005 | Yes | 780
10 | 8:30 | 1.64 | 65 | 106.6 | 12.2 | 7.1 | 18.5944 | Yes | 440
11 | 10:00 | 1.5 | 65 | 97.5 | 11.9 | 7.1 | 18.6671 | Yes | 800
12 | 9:30 | 1.52 | 65 | 98.8 | 11.8 | 7.1 | 18.83 | Yes | 140
13 | 10:15 | 1.46 | 65 | 94.9 | 12.1 | 7.1 | 18.3459 | Yes | 140
14 | 9:15 | 1.42 | 65 | 92.3 | 12.1 | 7.13 | 18.4545 | Yes | 800
15 | 10:00 | 1.48 | 65 | 96.2 | 12.5 | 7.09 | 17.5716 | Yes | 800
16 | 9:50 | 1.52 | 65 | 98.8 | 12.4 | 7.14 | 18.3647 | Yes | 750
17 | 9:30 | 1.52 | 65 | 98.8 | 13 | 7.16 | 17.5215 | Yes | 790
18 | 9:00 | 1.24 | 65 | 80.6 | 12.5 | 7.4 | 19.172 | Yes | 740
19 | 10:00 | 1.2 | 65 | 78 | 12.9 | 7.3 | 17.9116 | Yes | 150
20 | 9:30 | 1.18 | 65 | 76.7 | 12.2 | 7.1 | 17.6738 | Yes | 140
21 | 10:00 | 1.1 | 65 | 71.5 | 12.6 | 7.1 | 16.7793 | Yes | 900
22 | 9:00 | 1.42 | 65 | 92.3 | 12.8 | 7.1 | 17.1707 | Yes | 790
23 | 9:30 | 1.36 | 65 | 88.4 | 11 | 6.93 | 18.373 | Yes | 740
24 | 8:00 | 1.34 | 65 | 87.1 | 12.1 | 7 | 17.4944 | Yes | 740
25 | 9:00 | 1.26 | 65 | 81.9 | 11.7 | 7.1 | 18.4142 | Yes | 160
26 | 9:30 | 1.2 | 65 | 78 | 12.3 | 6.97 | 16.8359 | Yes | 140
27 | 9:00 | 1.38 | 65 | 89.7 | 11.9 | 6.9 | 17.2005 | Yes | 130
28 | 7:30 | 1.1 | 65 | 71.5 | 12.2 | 6.9 | 16.3663 | Yes | 800
29 | 15:30 | 1 | 65 | 65 | 11.1 | 7.1 | 18.5994 | Yes | 810
30 | 8:45 | 1.18 | 65 | 76.7 | 12.2 | 7.1 | 17.6738 | Yes | 130
| 3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2