## Turbidity Monitoring Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Yamhill
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-12-22
System Name: | City of Sheridan |  |  | ID#: 41 | 00811 |  | WTP : | WTP-A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | 0.051 | 0.051 | 0.05 | OFF | 0.053
2 | OFF | OFF | 0.046 | 0.09 | OFF | OFF | 0.1
3 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
4 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
5 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
6 | OFF | OFF | 0.083 | 0.092 | 0.09 | OFF | 0.094
7 | OFF | OFF | 0.09 | 0.088 | 0.085 | OFF | 0.093
8 | OFF | OFF | 0.075 | 0.077 | 0.075 | OFF | 0.075
9 | OFF | OFF | 0.5 | 0.11 | 0.5 | OFF | 0.11
10 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
11 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
12 | OFF | OFF | 0.099 | 0.087 | 0.085 | OFF | 0.1
13 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
14 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
15 | OFF | OFF | 0.038 | 0.11 | 0.122 | OFF | 0.28
16 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
17 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
18 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
19 | OFF | OFF | 0.11 | 0.104 | 0.108 | OFF | 0.126
20 | OFF | OFF | 0.098 | 0.072 | OFF | OFF | 0.27
21 | OFF | OFF | 0.074 | 0.07 | 0.069 | OFF | 0.075
22 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
23 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
24 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
25 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
26 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
27 | OFF | OFF | 0.088 | OFF | OFF | OFF | 0.088
28 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
29 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
30 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
31 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | √ Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | √ Yes / No
All turbidity readings < IFE2 triggers |  |  |  | √ Yes / No | √ Yes / No |  | √ Yes / No
Notes: |  |  |  |  | PRINTED NAME: Gary N Mathis
[5 empty] | SIGNATURE: |  |  | DATE:1/12/23
[5 empty] | PHONE #: (971)312-1892 |  |  | CERT #:127558
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Surface Water Quality Data
| OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | WTP-A
System Name: |  | City of Sheridan |  | ID#: 41 00811 |  | Month/Year: | 2022-12-22 | Disinfection Giardia Log Inactiv: | 0.5
Date | Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
|  | [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 7:45 | 0.59 | 65 | 38.35 | 12.3 | 6.93 | 15.545 | Yes | 620
2 | 8:15 | 0.6 | 65 | 39 | 12.2 | 6.91 | 15.5553 | Yes | 760
3 | 9:00 | 0.57 | 65 | 37.05 | 12 | 6.81 | 15.1837 | Yes | OFF
4 | 9:22 | 0.62 | 65 | 40.3 | 11.4 | 6.82 | 15.9077 | Yes | OFF
5 | 10:00 | 0.66 | 65 | 42.9 | 12.7 | 7 | 15.2774 | Yes | OFF
6 | 7:30 | 0.57 | 65 | 37.05 | 11.4 | 7.05 | 17.1043 | Yes | 860
7 | 7:30 | 0.61 | 65 | 39.65 | 11.8 | 6.8 | 15.3905 | Yes | 880
8 | 8:00 | 0.55 | 65 | 35.75 | 11.4 | 6.8 | 15.6817 | Yes | 840
9 | 8:15 | 0.56 | 65 | 36.4 | 11.3 | 6.8 | 15.7981 | Yes | 640
10 | 8:00 | 0.58 | 65 | 37.7 | 11.1 | 6.8 | 16.034 | Yes | OFF
11 | 7:45 | 0.83 | 65 | 53.95 | 10.6 | 7.1 | 18.8526 | Yes | OFF
12 | 15:15 | 0.91 | 65 | 59.15 | 10.8 | 7.1 | 18.7758 | Yes | 500
13 | 11:00 | 0.73 | 65 | 47.45 | 10.2 | 7.6 | 22.7877 | Yes | OFF
14 | 7:00 | 0.52 | 65 | 33.8 | 10.9 | 7.1 | 17.8679 | Yes | OFF
15 | 8:30 | 0.5 | 65 | 32.5 | 14.2 | 7 | 13.5698 | Yes | 840
16 | 9:00 | 0.5 | 65 | 32.5 | 11 | 7 | 17.1193 | Yes | OFF
17 | 9:30 | 0.57 | 65 | 37.05 | 10.8 | 7.4 | 20.0587 | Yes | OFF
18 | 10:30 | 0.53 | 65 | 34.45 | 11 | 7.2 | 18.3938 | Yes | OFF
19 | 9:00 | 0.55 | 65 | 35.75 | 12 | 7.1 | 16.7073 | Yes | 880
20 | 10:00 | 0.72 | 65 | 46.8 | 11.1 | 7.1 | 18.0325 | Yes | 860
21 | 10:25 | 0.48 | 65 | 31.2 | 10.7 | 7.1 | 18.0198 | Yes | 580
22 | 9:15 | 0.85 | 65 | 55.25 | 10.5 | 7 | 18.3727 | Yes | OFF
23 | 9:15 | 0.81 | 65 | 52.65 | 9.9 | 6.9 | 18.3711 | Yes | OFF
24 | 9:00 | 0.77 | 65 | 50.05 | 9.6 | 6.96 | 19.0384 | Yes | OFF
25 | 9:30 | 0.73 | 65 | 47.45 | 9.4 | 6.99 | 19.4021 | Yes | OFF
26 | 7:30 | 0.65 | 65 | 42.25 | 13.4 | 6.9 | 14.0322 | Yes | OFF
27 | 8:30 | 0.55 | 65 | 35.75 | 12.7 | 7 | 15.087 | Yes | 540
28 | 8:00 | 0.73 | 65 | 47.45 | 11.7 | 7.1 | 17.3696 | Yes | OFF
29 | 8:15 | 1.48 | 65 | 96.2 | 10.6 | 6.6 | 17.0609 | Yes | OFF
30 | 8:45 | 0.77 | 65 | 50.05 | 12.8 | 6.8 | 14.2684 | Yes | OFF
31 | 9:20 | 0.93 | 65 | 60.45 | 11.6 | 6.7 | 15.6005 | Yes | OFF
| 3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2