## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | May_21
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
2 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
3 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
4 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
5 | 0.02 | OFF | OFF | 0.02 | OFF | 0.02 | 0.02
6 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
7 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
8 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
9 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
10 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
11 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
12 | 0.02 | 0.02 | OFF | OFF | 0.02 | OFF | 0.02
13 | 0.02 | 0.02 | OFF | 0.02 | OFF | OFF | 0.02
14 | 0.02 | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
15 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
16 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
17 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
18 | OFF | OFF | OFF | OFF | 0.02 | 0.02 | 0.02
19 | 0.02 | OFF | 0.05 | OFF | OFF | 0.02 | 0.02
20 | 0.02 | 0.02 | 0.02 | OFF | 0.02 | OFF | 0.02
21 | 0.02 | 0.02 | 0.02 | OFF | 0.02 | OFF | 0.02
22 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02 | 0.02
23 | 0.02 | OFF | 0.07 | 0.02 | 0.02 | OFF | 0.07
24 | 0.02 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02
25 | OFF | 0.02 | 0.02 | 0.02 | OFF | OFF | 0.02
26 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
27 | OFF | 0.02 | 0.04 | 0.02 | 0.02 | OFF | 0.04
28 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
29 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
30 | 0.02 | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
31 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Ricardo R. Saavedra
[5 empty] | SIGNATURE: Ricardo r.Saavedra |  |  | DATE:06/04/2021
[5 empty] | PHONE #: (541) 336-2610 |  |  | CERT #:T-09181
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | May_21 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 20:00 | 0.78 | 111 | 86.58 | 12.1 | 7.3 | 18.2295 | YES | 882
2 / 8:00 | 0.77 | 111 | 85.47 | 13.1 | 7.38 | 17.3373 | YES | 896
3 / 8:00 | 0.77 | 111 | 85.47 | 13.2 | 7.35 | 17.0324 | YES | 877
4 / 8:00 | 0.77 | 111 | 85.47 | 13.4 | 7.4 | 17.1207 | YES | 851
5 / 12:00 | 0.79 | 111 | 87.69 | 13.6 | 7.36 | 16.6841 | YES | 818
6 / 8:00 | 0.76 | 111 | 84.36 | 13.8 | 7.49 | 17.2153 | YES | 806
7 / 20:00 | 0.74 | 111 | 82.14 | 13.7 | 7.63 | 18.2083 | YES | 838
8 / 8:00 | 0.75 | 111 | 83.25 | 13.4 | 7.62 | 18.5275 | YES | 885
9 / 20:00 | 0.75 | 111 | 83.25 | 13.3 | 7.67 | 18.9981 | YES | 874
10 / 16:00 | 0.72 | 111 | 79.92 | 13.1 | 7.55 | 18.356 | YES | 1039
11 / 8:00 | 0.67 | 111 | 74.37 | 13.2 | 7.5 | 17.7996 | YES | 977
12 / 16:00 | 0.67 | 111 | 74.37 | 13.6 | 7.41 | 16.7652 | YES | 986
13 / 12:00 | 0.68 | 111 | 75.48 | 13.9 | 7.22 | 15.3346 | YES | 842
14 / 8:00 | 0.73 | 111 | 81.03 | 14.7 | 7.28 | 14.9491 | YES | 888
15 / 20:00 | 0.78 | 111 | 86.58 | 15 | 7.5 | 15.9882 | YES | 883
16 / 8:00 | 0.77 | 111 | 85.47 | 15.2 | 7.41 | 15.2416 | YES | 880
17 / 8:00 | 0.76 | 111 | 84.36 | 15.8 | 7.33 | 14.1984 | YES | 903
18 / 20:00 | 0.72 | 111 | 79.92 | 15.1 | 7.33 | 14.8106 | YES | 1002
19 / 8:00 | 0.66 | 111 | 73.26 | 14.9 | 7.41 | 15.3562 | YES | 812
20 / 16:00 | 0.71 | 111 | 78.81 | 14.5 | 7.55 | 16.7048 | YES | 823
21 / 24:00 | 0.71 | 111 | 78.81 | 14.4 | 7.57 | 16.9412 | YES | 833
22 / 4:00 | 0.75 | 111 | 83.25 | 13.9 | 7.63 | 17.9883 | YES | 847
23 / 24:00 | 0.77 | 111 | 85.47 | 13.8 | 7.48 | 17.1712 | YES | 845
24 / 16:00 | 0.77 | 111 | 85.47 | 13.7 | 7.54 | 17.6733 | YES | 885
25 / 4:00 | 0.74 | 111 | 82.14 | 13.7 | 7.4 | 16.725 | YES | 865
26 / 16:00 | 0.74 | 111 | 82.14 | 13.6 | 7.48 | 17.3421 | YES | 862
27 / 4:00 | 0.72 | 111 | 79.92 | 13.4 | 7.21 | 15.8681 | YES | 838
28 / 24:00 | 0.7 | 111 | 77.7 | 14 | 7.28 | 15.6106 | YES | 834
29 / 20:00 | 0.71 | 111 | 78.81 | 14.1 | 7.38 | 16.1101 | YES | 849
30 / 16:00 | 0.73 | 111 | 81.03 | 14.4 | 7.5 | 16.5459 | YES | 889
31 / 16:00 | 0.72 | 111 | 79.92 | 15 | 7.44 | 15.5304 | YES | 844
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | May | 0.04059 | 999.99 | 0.039805 | 0.042729 | 999.99 | 0.041552 | 0 | 0 | 0.043672 | 0.79668 | 999.99 | 0.78902 | 0.7922 | 999.99 | 0.78202 | 20 | 0.78202 | 0.78
2 | May | 999.99 | 999.99 | 0.044437 | 0.039785 | 999.99 | 999.99 | 8 | 0 | 0.044516 | 999.99 | 999.99 | 0.77236 | 0.79827 | 999.99 | 999.99 | 8 | 0.77236 | 0.77
3 | May | 0.03794 | 999.99 | 0.039137 | 1.0011 | 999.99 | 999.99 | 12 | 0 | 1.0023 | 0.79356 | 999.99 | 0.77424 | 0.79261 | 999.99 | 999.99 | 8 | 0.77424 | 0.77
4 | May | 0.58681 | 999.99 | 0.53844 | 0.50757 | 0.41348 | 0.41034 | 0 | 0 | 0.60667 | 0.77306 | 999.99 | 0.77348 | 0.78466 | 0.78961 | 0.79544 | 8 | 0.77348 | 0.77
5 | May | 0.42819 | 999.99 | 999.99 | 0.33593 | 999.99 | 999.99 | 0 | 0 | 0.42823 | 0.80257 | 999.99 | 999.99 | 0.78702 | 999.99 | 999.99 | 12 | 0.78702 | 0.79
6 | May | 0.34402 | 999.99 | 0.35585 | 0.31471 | 999.99 | 999.99 | 8 | 0 | 0.35852 | 0.77748 | 999.99 | 0.75758 | 0.78555 | 999.99 | 999.99 | 8 | 0.75758 | 0.76
7 | May | 0.34569 | 999.99 | 0.33556 | 0.32655 | 999.99 | 0.30285 | 0 | 0 | 0.34569 | 0.75958 | 999.99 | 0.75351 | 0.77442 | 999.99 | 0.73867 | 20 | 0.73867 | 0.74
8 | May | 999.99 | 999.99 | 0.27849 | 0.25629 | 0.23566 | 999.99 | 8 | 0 | 0.27849 | 999.99 | 999.99 | 0.7561 | 0.76806 | 0.77707 | 999.99 | 8 | 0.7561 | 0.76
9 | May | 0.23635 | 999.99 | 0.22308 | 0.20744 | 999.99 | 0.20905 | 0 | 0 | 0.23983 | 0.7657 | 999.99 | 0.75086 | 0.7723 | 999.99 | 0.75569 | 20 | 0.75086 | 0.75
10 | May | 999.99 | 999.99 | 999.99 | 0.19012 | 0.1768 | 999.99 | 12 | 0 | 0.19152 | 999.99 | 999.99 | 999.99 | 0.73779 | 0.72354 | 999.99 | 16 | 0.72354 | 0.72
11 | May | 0.17752 | 999.99 | 0.19393 | 0.16537 | 0.16439 | 999.99 | 8 | 0 | 0.19393 | 0.68214 | 999.99 | 0.66913 | 0.68856 | 0.69786 | 999.99 | 8 | 0.66913 | 0.67
12 | May | 0.16469 | 0.17191 | 999.99 | 999.99 | 0.039471 | 999.99 | 4 | 0 | 0.17211 | 0.69351 | 0.69068 | 999.99 | 999.99 | 0.66766 | 999.99 | 16 | 0.66766 | 0.67
13 | May | 0.040884 | 0.039177 | 999.99 | 0.043711 | 999.99 | 999.99 | 12 | 0 | 0.049541 | 0.67372 | 0.69916 | 999.99 | 0.67566 | 999.99 | 999.99 | 12 | 0.67566 | 0.68
14 | May | 0.04006 | 999.99 | 0.044045 | 0.055763 | 0.039707 | 999.99 | 12 | 0 | 0.055901 | 0.73231 | 999.99 | 0.73161 | 0.76812 | 0.79085 | 999.99 | 8 | 0.73161 | 0.73
15 | May | 999.99 | 0.043554 | 0.041041 | 0.043809 | 999.99 | 0.041179 | 20 | 0 | 0.044476 | 999.99 | 0.77966 | 0.78537 | 0.79632 | 999.99 | 0.77819 | 20 | 0.77819 | 0.78
16 | May | 999.99 | 999.99 | 0.043907 | 0.041453 | 999.99 | 0.21468 | 20 | 0 | 0.22601 | 999.99 | 999.99 | 0.77041 | 0.78031 | 999.99 | 0.77571 | 8 | 0.77041 | 0.77
17 | May | 999.99 | 999.99 | 0.044123 | 0.04165 | 999.99 | 999.99 | 8 | 0 | 0.046812 | 999.99 | 999.99 | 0.7597 | 0.78525 | 999.99 | 999.99 | 8 | 0.7597 | 0.76
18 | May | 999.99 | 999.99 | 999.99 | 0.060258 | 0.047283 | 0.048206 | 12 | 0 | 0.060258 | 999.99 | 999.99 | 999.99 | 0.73979 | 0.74062 | 0.72401 | 20 | 0.72401 | 0.72
19 | May | 0.04799 | 999.99 | 0.07288 | 999.99 | 999.99 | 0.04642 | 8 | 0 | 0.074941 | 0.70046 | 999.99 | 0.65829 | 999.99 | 999.99 | 0.67107 | 8 | 0.65829 | 0.66
20 | May | 0.04797 | 0.046282 | 0.045105 | 999.99 | 0.048775 | 999.99 | 0 | 0 | 0.049737 | 0.70263 | 0.72407 | 0.73814 | 999.99 | 0.7107 | 999.99 | 16 | 0.7107 | 0.71
21 | May | 0.049541 | 0.047911 | 0.05009 | 999.99 | 0.048873 | 999.99 | 16 | 0 | 0.050463 | 0.70905 | 0.72542 | 0.74598 | 999.99 | 0.73956 | 999.99 | 24 | 0.71 | 0.71
22 | May | 999.99 | 0.049933 | 0.050522 | 0.04799 | 999.99 | 0.051268 | 20 | 0 | 0.052622 | 999.99 | 0.74715 | 0.76859 | 0.77642 | 999.99 | 0.76358 | 4 | 0.74715 | 0.75
23 | May | 0.048991 | 999.99 | 0.090193 | 0.050463 | 0.048814 | 999.99 | 8 | 0 | 0.093117 | 0.77707 | 999.99 | 0.78537 | 0.80357 | 0.81476 | 999.99 | 24 | 0.77 | 0.77
24 | May | 0.051641 | 0.048834 | 999.99 | 0.052426 | 0.052662 | 999.99 | 4 | 0 | 0.059179 | 0.78932 | 0.78961 | 999.99 | 0.76871 | 0.76588 | 999.99 | 16 | 0.76588 | 0.77
25 | May | 999.99 | 0.052799 | 0.050679 | 0.053545 | 999.99 | 999.99 | 4 | 0 | 0.058158 | 999.99 | 0.73962 | 0.74403 | 0.75122 | 999.99 | 999.99 | 4 | 0.73962 | 0.74
26 | May | 0.051484 | 0.058079 | 0.053839 | 0.053113 | 0.055292 | 999.99 | 4 | 0 | 0.058079 | 0.74421 | 0.74238 | 0.74592 | 0.74074 | 0.7375 | 999.99 | 16 | 0.7375 | 0.74
27 | May | 999.99 | 0.055253 | 0.070034 | 0.054919 | 0.054271 | 999.99 | 8 | 0 | 0.073174 | 999.99 | 0.72389 | 0.72254 | 0.73061 | 0.72925 | 999.99 | 4 | 0.72254 | 0.72
28 | May | 0.057805 | 999.99 | 0.056666 | 0.05647 | 0.055802 | 999.99 | 0 | 0 | 0.058629 | 0.70523 | 999.99 | 0.70858 | 0.72478 | 0.7478 | 999.99 | 24 | 0.7 | 0.7
29 | May | 0.056156 | 0.057196 | 0.055586 | 0.058393 | 0.054939 | 0.057667 | 20 | 0 | 0.058747 | 0.73149 | 0.73349 | 0.72766 | 0.73761 | 0.72961 | 0.7087 | 20 | 0.7087 | 0.71
30 | May | 0.058747 | 999.99 | 0.055508 | 0.059434 | 0.060965 | 0.061357 | 16 | 0 | 0.063595 | 0.73296 | 999.99 | 0.7352 | 0.73261 | 0.72684 | 0.73626 | 16 | 0.72684 | 0.73
31 | May | 999.99 | 0.061004 | 0.056862 | 0.056823 | 0.057019 | 0.058904 | 4 | 0 | 0.061122 | 999.99 | 0.72637 | 0.72219 | 0.73549 | 0.71965 | 0.73161 | 16 | 0.71965 | 0.72