## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Nov_21
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.04 | OFF | 0 | 0.02 | 0.02 | OFF | 0.04
2 | OFF | 0.02 | 0.024906 | 0.024965 | 0.024612 | 0.02 | 0.02
3 | 0.02 | OFF | 0.02 | OFF | OFF | 0.02 | 0.02
4 | OFF | OFF | 0.02 | 0.03 | 0.05 | OFF | 0.05
5 | 0.05 | 0.05 | 0.06 | 0.033425 | OFF | 0.02 | 0.06
6 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
7 | OFF | OFF | 0.02 | 0.03 | 0.04 | 0.05 | 0.05
8 | OFF | OFF | 0.047342 | 0.03 | 0.02 | OFF | 0.05
9 | 0.034348 | OFF | OFF | 0.042023 | 0.032032 | 0.031187 | 0.034466
10 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
11 | OFF | 0.02 | 0.03 | OFF | 0.05 | OFF | 0.05
12 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
13 | OFF | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02
14 | 0.02 | 0.02 | 0.02 | 0.02 | 0.04 | 0.02 | 0.04
15 | 0.02 | OFF | OFF | OFF | 0.03 | 0.03 | 0.03
16 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | OFF | 0.03
17 | OFF | OFF | OFF | 0.05 | 0.03 | 0.03 | 0.03
18 | 0.03 | 0.04 | 0.04 | 0.02 | 0.02 | 0.02 | 0.04
19 | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02
20 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
21 | 0.02 | OFF | 0.02 | 0.02 | 0.03 | 0.02 | 0.03
22 | OFF | 0.02 | 0.02 | 0.02 | OFF | OFF | 0.02
23 | 0.02 | 0.02 | 0.02 | 0.02 | OFF | OFF | 0.02
24 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
25 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
26 | OFF | 0.02 | 0.03 | 0.02 | OFF | OFF | 0.03
27 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
28 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
29 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
30 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Ricardo r. Saavedra
[5 empty] | SIGNATURE: Ricardo R.Saavedra |  |  | DATE:12/02/2021
[5 empty] | PHONE #: (541 ) 336-2610 |  |  | CERT #:T-09181
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Nov_21 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 16:00 | 0.86 | 111 | 95.46 | 11.6 | 7.38 | 19.5298 | YES | 865
2 / 8:00 | 0.83 | 111 | 92.13 | 11.4 | 7.54 | 20.85 | YES | 881
3 / 20:00 | 0.8 | 111 | 88.8 | 11.2 | 7.4 | 20.0507 | YES | 905
4 / 8:00 | 0.8 | 111 | 88.8 | 11.4 | 7.5 | 20.4918 | YES | 897
5 / 20:00 | 0.81 | 111 | 89.91 | 11.5 | 7.53 | 20.5953 | YES | 844
6 / 8:00 | 0.79 | 111 | 87.69 | 11.7 | 7.58 | 20.6388 | YES | 820
7 / 8:00 | 0.79 | 111 | 87.69 | 11.3 | 7.47 | 20.3888 | YES | 835
8 / 0:00 | 0.86 | 111 | 95.46 | 11 | 7.45 | 20.8114 | YES | 875
9 / 0:00 | 0.84 | 111 | 93.24 | 10.6 | 7.43 | 21.1685 | YES | 895
10 / 20:00 | 0.87 | 111 | 96.57 | 10.4 | 7.02 | 18.6609 | YES | 886
11 / 8:00 | 0.83 | 111 | 92.13 | 10.8 | 7.35 | 20.2944 | YES | 823
12 / 20:00 | 0.68 | 111 | 75.48 | 11.5 | 7.58 | 20.6545 | YES | 783
13 / 4:00 | 0.69 | 111 | 76.59 | 11.6 | 7.44 | 19.5662 | YES | 800
14 / 20:00 | 0.69 | 111 | 76.59 | 11.7 | 7.44 | 19.4393 | YES | 807
15 / 20:00 | 0.64 | 111 | 71.04 | 11.6 | 7.33 | 18.7312 | YES | 846
16 / 12:00 | 0.54 | 111 | 59.94 | 10.1 | 7.23 | 19.725 | YES | 815
17 / 16:00 | 0.56 | 111 | 62.16 | 10.7 | 7.18 | 18.6873 | YES | 844
18 / 24:00 | 0.69 | 111 | 76.59 | 10.6 | 7.34 | 20.1714 | YES | 778
19 / 20:00 | 0.96 | 111 | 106.56 | 10.4 | 7.42 | 21.6646 | YES | 802
20 / 20:00 | 0.9 | 111 | 99.9 | 10.4 | 7.5 | 22.1317 | YES | 773
21 / 8:00 | 0.88 | 111 | 97.68 | 10.2 | 7.5 | 22.3754 | YES | 818
22 / 8:00 | 0.91 | 111 | 101.01 | 9.7 | 7.71 | 25.0023 | YES | 814
23 / 4:00 | 0.89 | 111 | 98.79 | 10.2 | 7.64 | 23.5359 | YES | 837
24 / 20:00 | 0.84 | 111 | 93.24 | 9.7 | 7.53 | 23.269 | YES | 826
25 / 12:00 | 0.81 | 111 | 89.91 | 9.3 | 7.49 | 23.4792 | YES | 795
26 / 12:00 | 0.79 | 111 | 87.69 | 9.4 | 7.43 | 22.7829 | YES | 773
27 / 8:00 | 0.78 | 111 | 86.58 | 9.6 | 7.35 | 21.8348 | YES | 806
28 / 12:00 | 0.76 | 111 | 84.36 | 9.7 | 7.35 | 21.6425 | YES | 795
29 / 8:00 | 0.74 | 111 | 82.14 | 9.9 | 7.31 | 21.0152 | YES | 824
30 / 12:00 | 0.73 | 111 | 81.03 | 9.8 | 7.33 | 21.2783 | YES | 821
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Nov | 0.053938 | 999.99 | 0.054507 | 0.027772 | 0.025122 | 999.99 | 8 | 0 | 0.055959 | 0.88766 | 999.99 | 0.8631 | 0.8611 | 0.85816 | 999.99 | 16 | 0.85816 | 0.86
2 | Nov | 999.99 | 0.026359 | 0.024906 | 0.024965 | 0.024612 | 0.02681 | 20 | 0 | 0.028341 | 999.99 | 0.83613 | 0.83007 | 0.84226 | 0.83501 | 0.84025 | 8 | 0.83007 | 0.83
3 | Nov | 0.0284 | 999.99 | 0.02944 | 0.031325 | 999.99 | 0.036978 | 20 | 0 | 0.038725 | 0.84126 | 999.99 | 0.82188 | 0.82995 | 999.99 | 0.80104 | 20 | 0.80104 | 0.8
4 | Nov | 999.99 | 999.99 | 0.031973 | 0.050679 | 0.065303 | 999.99 | 16 | 0 | 0.068679 | 999.99 | 999.99 | 0.78767 | 0.81593 | 0.84773 | 999.99 | 8 | 0.78767 | 0.79
5 | Nov | 0.062103 | 0.095924 | 0.058119 | 0.033425 | 999.99 | 0.033288 | 4 | 0 | 0.10148 | 0.83319 | 0.83914 | 0.83543 | 0.83319 | 999.99 | 0.80374 | 20 | 0.80374 | 0.8
6 | Nov | 0.027399 | 999.99 | 0.030952 | 0.030893 | 999.99 | 999.99 | 8 | 0 | 0.030952 | 0.82041 | 999.99 | 0.78979 | 0.82347 | 999.99 | 999.99 | 8 | 0.78979 | 0.79
7 | Nov | 0.073704 | 999.99 | 0.031246 | 0.041139 | 0.045772 | 0.063831 | 0 | 0 | 0 | 0.85939 | 999.99 | 0.79067 | 0.81894 | 0.82383 | 0.85109 | 8 | 0.79067 | 0.79
8 | Nov | 0.029283 | 999.99 | 0.047342 | 0.15587 | 0.034642 | 999.99 | 0 | 0 | 0.03315 | 0.85969 | 999.99 | 0.84326 | 0.85274 | 0.86116 | 999.99 | 0 | 0.861 | 0.86
9 | Nov | 0.034348 | 999.99 | 999.99 | 0.042023 | 0.032032 | 0.031187 | 0 | 0 | 0.034466 | 0.89608 | 999.99 | 999.99 | 0.86269 | 0.88907 | 0.88377 | 0 | 0.843 | 0.84
10 | Nov | 999.99 | 999.99 | 0.033779 | 0.037096 | 999.99 | 0.037115 | 0 | 0 | 0 | 999.99 | 999.99 | 0.89973 | 0.8919 | 999.99 | 0.86546 | 20 | 0.86546 | 0.87
11 | Nov | 999.99 | 0.044692 | 0.063909 | 999.99 | 0.062084 | 999.99 | 8 | 0 | 0.065264 | 999.99 | 0.84096 | 0.83613 | 999.99 | 0.84061 | 999.99 | 8 | 0.83613 | 0.84
12 | Nov | 999.99 | 0.040178 | 0.036919 | 0.037881 | 0.041493 | 0.041964 | 20 | 0 | 0.04216 | 999.99 | 0.75287 | 0.7223 | 0.71088 | 0.68515 | 0.68038 | 20 | 0.68038 | 0.68
13 | Nov | 999.99 | 0.041885 | 999.99 | 0.038372 | 0.042023 | 999.99 | 4 | 0 | 0.042141 | 999.99 | 0.68538 | 999.99 | 0.714 | 0.71259 | 999.99 | 4 | 0.68538 | 0.69
14 | Nov | 0.043181 | 0.04059 | 0.039922 | 0.04324 | 0.062143 | 0.043573 | 16 | 0 | 0.063733 | 0.70146 | 0.70776 | 0.70128 | 0.69686 | 0.69857 | 0.68485 | 20 | 0.68485 | 0.68
15 | Nov | 0.043927 | 999.99 | 999.99 | 999.99 | 0.055645 | 0.048559 | 16 | 0 | 0.055665 | 0.69374 | 999.99 | 999.99 | 999.99 | 0.76241 | 0.64245 | 20 | 0.64245 | 0.64
16 | Nov | 0.047323 | 0.046793 | 0.054232 | 0.043534 | 0.044202 | 999.99 | 8 | 0 | 0.054232 | 0.60153 | 0.56007 | 0.5394 | 0.53634 | 0.55919 | 999.99 | 12 | 0.53634 | 0.54
17 | Nov | 999.99 | 999.99 | 999.99 | 999.99 | 0.058708 | 0.057157 | 20 | 0 | 0.060003 | 999.99 | 999.99 | 999.99 | 999.99 | 0.55765 | 0.60818 | 16 | 0.55765 | 0.56
18 | Nov | 0.0591 | 0.081379 | 0.075667 | 0.050365 | 0.052191 | 0.052289 | 4 | 0 | 0.083165 | 0.68562 | 0.76859 | 0.84367 | 0.89838 | 0.96357 | 0.99978 | 24 | 0.68562 | 0.69
19 | Nov | 999.99 | 0.054212 | 999.99 | 0.0538 | 0.053643 | 0.057687 | 4 | 0 | 0.058138 | 999.99 | 0.98123 | 999.99 | 0.98765 | 0.98135 | 0.95738 | 20 | 0.95738 | 0.96
20 | Nov | 999.99 | 999.99 | 0.060474 | 0.059237 | 999.99 | 0.062005 | 20 | 0 | 0.064282 | 999.99 | 999.99 | 0.91074 | 0.91392 | 999.99 | 0.8952 | 20 | 0.8952 | 0.9
21 | Nov | 0.06281 | 999.99 | 0.067148 | 0.0644 | 0.067658 | 0.068561 | 16 | 0 | 0.071074 | 0.89302 | 999.99 | 0.87423 | 0.90432 | 0.91339 | 0.92111 | 8 | 0.87423 | 0.87
22 | Nov | 999.99 | 0.06811 | 0.071329 | 0.068208 | 999.99 | 999.99 | 12 | 0 | 0.071938 | 999.99 | 0.91145 | 0.91086 | 0.92105 | 999.99 | 999.99 | 8 | 0.91086 | 0.91
23 | Nov | 0.070779 | 0.07076 | 0.072291 | 0.07233 | 999.99 | 999.99 | 4 | 0 | 0.073115 | 0.89814 | 0.89467 | 0.90468 | 0.8959 | 999.99 | 999.99 | 4 | 0.89467 | 0.89
24 | Nov | 0.073842 | 999.99 | 0.08026 | 0.079809 | 0.080358 | 0.082459 | 20 | 0 | 0.083146 | 0.87576 | 999.99 | 0.84449 | 0.84514 | 0.84137 | 0.83678 | 20 | 0.83678 | 0.84
25 | Nov | 0.085187 | 999.99 | 0.085855 | 0.087209 | 0.084481 | 0.083165 | 8 | 0 | 0.088956 | 0.81982 | 999.99 | 0.81222 | 0.80804 | 0.82265 | 0.81417 | 12 | 0.80804 | 0.81
26 | Nov | 999.99 | 0.087876 | 0.090075 | 0.088976 | 999.99 | 999.99 | 8 | 0 | 0.090212 | 999.99 | 0.7932 | 0.7872 | 0.78655 | 999.99 | 999.99 | 12 | 0.78655 | 0.79
27 | Nov | 0.087327 | 999.99 | 0.090782 | 0.087052 | 0.08768 | 999.99 | 12 | 0 | 0.091312 | 0.78219 | 999.99 | 0.78225 | 0.79432 | 0.79326 | 999.99 | 8 | 0.78225 | 0.78
28 | Nov | 0.091704 | 999.99 | 0.089604 | 0.04059 | 0.044535 | 999.99 | 8 | 0 | 0.092234 | 0.76971 | 999.99 | 0.75911 | 0.77242 | 0.75781 | 999.99 | 12 | 0.75781 | 0.76
29 | Nov | 0.045576 | 999.99 | 0.04854 | 0.049776 | 0.050051 | 0.046851 | 12 | 0 | 0.051209 | 0.7458 | 999.99 | 0.74698 | 0.76782 | 0.76229 | 0.75887 | 8 | 0.74698 | 0.75
30 | Nov | 999.99 | 999.99 | 0.048245 | 0.04852 | 0.051621 | 0.04905 | 16 | 0 | 0.051994 | 999.99 | 999.99 | 0.73491 | 0.72507 | 0.72584 | 0.73284 | 12 | 0.72507 | 0.73