## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Dec_21
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
2 | OFF | 0.02 | OFF | 0.02 | OFF | OFF | 0.02
3 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
4 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
5 | 0.02 | OFF | 0.02 | 0.02 | 0.2 | OFF | 0.02
6 | 0.02 | OFF | 0.02 | 0.02 | 0.03 | OFF | 0.03
7 | 0.03 | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
8 | 0.04 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
9 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
10 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
11 | OFF | OFF | 0.032758 | 0.03 | OFF | 0.02 | 0.03
12 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
13 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
14 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
15 | 0.02 | OFF | 0.02 | OFF | OFF | 0.02 | 0.02
16 | OFF | 0.02 | 0.02 | 0.02 | OFF | OFF | 0.02
17 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
18 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
19 | OFF | 0.02 | 0.02 | OFF | 0.02 | OFF | 0.02
20 | 0.03 | 0.02 | 0.02 | OFF | OFF | 0.02 | 0.032247
21 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
22 | 0.02 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02
23 | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02
24 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
25 | 0.02 | OFF | 0.02 | 0.03 | 0.02 | 0.02 | 0.03
26 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
27 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
28 | 0.02 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
29 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02 | OFF | 0.03
30 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
31 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J Dues
[5 empty] | SIGNATURE:Zachary J Dues |  |  | DATE:01/03/2021
[5 empty] | PHONE #: (541) 336-2610 |  |  | CERT #:T-269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Dec_21 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 16:00 | 0.71 | 111 | 78.81 | 10.2 | 7.26 | 20.1819 | YES | 844
2 / 4:00 | 0.71 | 111 | 78.81 | 9.6 | 7.23 | 20.7717 | YES | 815
3 / 24:00 | 0.7 | 111 | 77.7 | 9.6 | 7.31 | 21.3372 | YES | 791
4 / 16:00 | 0.74 | 111 | 82.14 | 9.1 | 7.32 | 22.2296 | YES | 762
5 / 12:00 | 0.71 | 111 | 78.81 | 9.4 | 7.34 | 21.8734 | YES | 799
6 / 8:00 | 0.73 | 111 | 81.03 | 9.3 | 7.26 | 21.4567 | YES | 875
7 / 8:00 | 0.8 | 111 | 88.8 | 9.3 | 7.41 | 22.7988 | YES | 806
8 / 8:00 | 0.85 | 111 | 94.35 | 9.5 | 7.66 | 24.7214 | YES | 854
9 / 8:00 | 0.86 | 111 | 95.46 | 9.3 | 7.64 | 24.9046 | YES | 840
10 / 20:00 | 0.84 | 111 | 93.24 | 9.1 | 7.64 | 25.182 | YES | 787
11 / 20:00 | 0.8 | 111 | 88.8 | 9.1 | 7.54 | 24.1914 | YES | 771
12 / 8:00 | 0.79 | 111 | 87.69 | 9.2 | 7.54 | 24.0035 | YES | 757
13 / 12:00 | 0.81 | 111 | 89.91 | 9.2 | 7.48 | 23.5521 | YES | 766
14 / 8:00 | 0.79 | 111 | 87.69 | 9.1 | 7.39 | 22.9143 | YES | 856
15 / 8:00 | 0.81 | 111 | 89.91 | 9.7 | 7.42 | 22.3072 | YES | 834
16 / 8:00 | 0.85 | 111 | 94.35 | 9 | 7.57 | 24.7552 | YES | 824
17 / 24:00 | 0.86 | 111 | 95.46 | 9.1 | 7.67 | 25.5111 | YES | 858
18 / 20:00 | 0.86 | 111 | 95.46 | 9.2 | 7.64 | 25.0715 | YES | 799
19 / 16:00 | 0.84 | 111 | 93.24 | 9.2 | 7.56 | 24.3127 | YES | 814
20 / 20:00 | 0.82 | 111 | 91.02 | 9 | 7.51 | 24.1502 | YES | 784
21 / 16:00 | 0.82 | 111 | 91.02 | 9.2 | 7.48 | 23.5789 | YES | 848
22 / 20:00 | 0.81 | 111 | 89.91 | 9.2 | 7.48 | 23.5521 | YES | 824
23 / 12:00 | 0.79 | 111 | 87.69 | 9.3 | 7.45 | 23.0969 | YES | 812
24 / 16:00 | 0.77 | 111 | 85.47 | 9.1 | 7.42 | 23.1059 | YES | 849
25 / 12:00 | 0.76 | 111 | 84.36 | 9.1 | 7.35 | 22.5166 | YES | 787
26 / 8:00 | 0.79 | 111 | 87.69 | 8.7 | 7.52 | 24.6411 | YES | 777
27 / 4:00 | 0.83 | 111 | 92.13 | 8.4 | 7.77 | 27.6182 | YES | 802
28 / 12:00 | 0.85 | 111 | 94.35 | 8.5 | 7.9 | 28.8124 | YES | 803
29 / 8:00 | 0.86 | 111 | 95.46 | 8.3 | 7.62 | 26.4402 | YES | 809
30 / 12:00 | 0.85 | 111 | 94.35 | 8.5 | 7.5 | 24.966 | YES | 833
31 / 8:00 | 0.86 | 111 | 95.46 | 8.1 | 7.55 | 26.1349 | YES | 823
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Dec | 999.99 | 999.99 | 0.050895 | 0.053447 | 0.052564 | 0.054212 | 20 | 0 | 0.054232 | 999.99 | 999.99 | 0.71848 | 0.72213 | 0.71235 | 0.71577 | 16 | 0.71235 | 0.71
2 | Dec | 999.99 | 0.062437 | 999.99 | 0.054154 | 999.99 | 999.99 | 4 | 0 | 0.066461 | 999.99 | 0.71147 | 999.99 | 0.70399 | 999.99 | 999.99 | 4 | 0.711 | 0.71
3 | Dec | 0.054684 | 999.99 | 0.055744 | 0.055253 | 0.056745 | 999.99 | 12 | 0 | 0.05806 | 0.70399 | 999.99 | 0.71265 | 0.7362 | 0.74527 | 999.99 | 24 | 0.704 | 0.7
4 | Dec | 999.99 | 0.056961 | 0.056784 | 0.058099 | 0.060396 | 999.99 | 4 | 0 | 0.060867 | 999.99 | 0.74144 | 0.74503 | 0.73856 | 0.7458 | 999.99 | 16 | 0.73856 | 0.74
5 | Dec | 0.060533 | 999.99 | 0.06124 | 0.058629 | 0.061416 | 999.99 | 0 | 0 | 0.063477 | 0.7279 | 999.99 | 0.70505 | 0.71029 | 0.72354 | 999.99 | 12 | 0.70505 | 0.71
6 | Dec | 0.060984 | 999.99 | 0.058413 | 0.06283 | 0.06385 | 999.99 | 16 | 0 | 0.066049 | 0.72931 | 999.99 | 0.72254 | 0.7375 | 0.76488 | 999.99 | 8 | 0.72254 | 0.72
7 | Dec | 0.063281 | 999.99 | 0.063281 | 0.06283 | 0.06495 | 999.99 | 0 | 0 | 0.066834 | 0.76871 | 999.99 | 0.79803 | 0.825 | 0.84974 | 999.99 | 8 | 0.79803 | 0.8
8 | Dec | 0.072546 | 999.99 | 0.065637 | 0.06601 | 999.99 | 0.065283 | 20 | 0 | 0.06864 | 0.84573 | 999.99 | 0.84603 | 0.86834 | 999.99 | 0.88053 | 8 | 0.84603 | 0.85
9 | Dec | 0.067168 | 999.99 | 0.068856 | 0.070622 | 999.99 | 999.99 | 12 | 0 | 0.071466 | 0.87983 | 999.99 | 0.85409 | 0.85692 | 999.99 | 999.99 | 8 | 0.85409 | 0.85
10 | Dec | 0.070603 | 999.99 | 0.071388 | 0.071309 | 0.034583 | 0.030756 | 12 | 0 | 0.07551 | 0.85186 | 999.99 | 0.88795 | 0.85551 | 0.84043 | 0.83843 | 20 | 0.83843 | 0.84
11 | Dec | 999.99 | 999.99 | 0.032758 | 0.035977 | 999.99 | 0.034485 | 8 | 0 | 0.036821 | 999.99 | 999.99 | 0.81464 | 0.80003 | 999.99 | 0.79097 | 20 | 0.79097 | 0.79
12 | Dec | 0.031855 | 999.99 | 0.034034 | 0.031874 | 999.99 | 999.99 | 0 | 0 | 0.035427 | 0.80639 | 999.99 | 0.78661 | 0.81411 | 999.99 | 999.99 | 8 | 0.78661 | 0.79
13 | Dec | 0.031639 | 999.99 | 0.033602 | 0.034485 | 999.99 | 999.99 | 12 | 0 | 0.034976 | 0.80386 | 999.99 | 0.80086 | 0.80787 | 999.99 | 999.99 | 12 | 0.81 | 0.81
14 | Dec | 0.033464 | 999.99 | 0.035997 | 0.032856 | 0.029303 | 0.029617 | 8 | 0 | 0.036625 | 0.79114 | 999.99 | 0.78637 | 0.80504 | 0.81063 | 0.81234 | 8 | 0.78637 | 0.79
15 | Dec | 0.028793 | 999.99 | 0.030677 | 999.99 | 999.99 | 0.030599 | 8 | 0 | 0.031129 | 0.82695 | 999.99 | 0.80751 | 999.99 | 999.99 | 0.81699 | 8 | 0.80751 | 0.81
16 | Dec | 999.99 | 0.029656 | 0.029225 | 0.028538 | 999.99 | 999.99 | 0 | 0 | 0.037606 | 999.99 | 0.83619 | 0.85545 | 0.86228 | 999.99 | 999.99 | 8 | 0.85 | 0.85
17 | Dec | 0.028047 | 999.99 | 0.031659 | 0.033582 | 0.035938 | 999.99 | 16 | 0 | 0.03845 | 0.86381 | 999.99 | 0.86569 | 0.87706 | 0.87035 | 999.99 | 24 | 0.86569 | 0.87
18 | Dec | 0.035584 | 0.051759 | 0.055528 | 0.032404 | 0.029813 | 0.029068 | 8 | 0 | 0.05857 | 0.8624 | 0.86499 | 0.86104 | 0.86758 | 0.86552 | 0.87258 | 20 | 0.86104 | 0.86
19 | Dec | 999.99 | 0.029146 | 0.030716 | 999.99 | 0.030579 | 999.99 | 16 | 0 | 0.032051 | 999.99 | 0.86016 | 0.8442 | 999.99 | 0.83201 | 999.99 | 16 | 0.83201 | 0.83
20 | Dec | 0.03582 | 0.031776 | 0.03052 | 999.99 | 999.99 | 0.031953 | 8 | 0 | 0.032247 | 0.83607 | 0.83525 | 0.83878 | 999.99 | 999.99 | 0.82235 | 20 | 0.82235 | 0.82
21 | Dec | 0.031835 | 0.028106 | 0.031816 | 0.031933 | 0.037017 | 999.99 | 16 | 0 | 0.037037 | 0.81947 | 0.82453 | 0.8154 | 0.8154 | 0.82394 | 999.99 | 16 | 0.8154 | 0.82
22 | Dec | 0.033131 | 0.030775 | 999.99 | 0.031286 | 0.02946 | 0.032189 | 0 | 0 | 0.034053 | 0.81116 | 0.81381 | 999.99 | 0.81864 | 0.81493 | 0.80286 | 20 | 0.80286 | 0.8
23 | Dec | 999.99 | 0.032876 | 999.99 | 0.029735 | 0.029656 | 0.034112 | 20 | 0 | 0.034132 | 999.99 | 0.79685 | 999.99 | 0.7915 | 0.79974 | 0.79273 | 12 | 0.7915 | 0.79
24 | Dec | 0.0337 | 999.99 | 0.03264 | 0.03315 | 0.031384 | 999.99 | 8 | 0 | 0.034662 | 0.78272 | 999.99 | 0.77024 | 0.77954 | 0.78567 | 999.99 | 16 | 0.77024 | 0.77
25 | Dec | 0.033445 | 999.99 | 0.033406 | 0.038509 | 0.034996 | 0.031619 | 12 | 0 | 0.03953 | 0.7617 | 999.99 | 0.76235 | 0.77094 | 0.78396 | 0.79715 | 12 | 0.76235 | 0.76
26 | Dec | 0.032463 | 999.99 | 0.031659 | 0.03209 | 0.02997 | 999.99 | 8 | 0 | 0.035388 | 0.80292 | 999.99 | 0.79933 | 0.82671 | 0.83018 | 999.99 | 8 | 0.79933 | 0.8
27 | Dec | 0.038627 | 0.030127 | 0.033936 | 0.0305 | 0.030579 | 999.99 | 8 | 0 | 0.036213 | 0.83225 | 0.84314 | 0.84126 | 0.84703 | 0.85963 | 999.99 | 4 | 0.84126 | 0.84
28 | Dec | 0.034093 | 999.99 | 999.99 | 0.035761 | 0.034466 | 999.99 | 16 | 0 | 0.037704 | 0.85462 | 999.99 | 999.99 | 0.8535 | 0.86705 | 999.99 | 12 | 0.8535 | 0.85
29 | Dec | 0.037469 | 0.044516 | 0.049855 | 0.032542 | 0.035957 | 999.99 | 8 | 0 | 0.051033 | 0.85574 | 0.8568 | 0.87229 | 0.8704 | 0.87376 | 999.99 | 8 | 0.8568 | 0.86
30 | Dec | 0.034937 | 999.99 | 0.036782 | 0.032758 | 0.036114 | 0.035643 | 8 | 0 | 0.036782 | 0.85262 | 999.99 | 0.84485 | 0.85562 | 0.87306 | 0.87017 | 12 | 0.84485 | 0.84
31 | Dec | 999.99 | 999.99 | 0.034642 | 0.033563 | 0.036095 | 0.033818 | 20 | 0 | 0.037057 | 999.99 | 999.99 | 0.872 | 0.86681 | 0.86617 | 0.86352 | 8 | 0.86352 | 0.86