## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Sep_22
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | OFF | 0.02 | OFF | OFF | 0.02 | 0.02
2 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02 | 0.02
3 | OFF | OFF | 0.02 | 0.03 | OFF | OFF | 0.03
4 | 0.02 | 0.02 | 0.02 | OFF | 0.02 | OFF | 0.02
5 | 0.02 | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
6 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
7 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
8 | OFF | OFF | 0.03 | OFF | 0.04 | 0.02 | 0.04
9 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
10 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
11 | 0.02 | OFF | 0.02 | 0.022767 | OFF | OFF | 0.02
12 | 0.024926 | OFF | 0.023041 | 0.022452 | OFF | 0.024985 | 0.02
13 | OFF | OFF | 0.026123 | 0.037665 | OFF | OFF | 0.037744
14 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
15 | OFF | 0.024199 | 0.024337 | 0.023022 | OFF | 0.02 | 0.02
16 | OFF | OFF | 0.024729 | 0.023787 | OFF | 0.02 | 0.02
17 | OFF | OFF | 0.02 | 0.04 | 0.02 | 2 | 0.04
18 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
19 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
20 | 0.023571 | OFF | 0.024965 | 0.02 | 0.02 | 0.02 | 0.02
21 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
22 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
23 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
24 | 0.02 | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
25 | OFF | OFF | 0.024474 | 0.03 | 0.02 | OFF | 0.03
26 | 0.02 | 0.02 | 0.02 | OFF | OFF | 0.02 | 0.02
27 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
28 | 0.02 | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
29 | OFF | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02
30 | OFF | OFF | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Zachary J Dues
[5 empty] | SIGNATURE: Zachary J Dues |  |  | DATE: 10/03/2022
[5 empty] | PHONE #: ( 541 ) 336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Sep_22 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 0:00 | 0.74 | 111 | 82.14 | 19.5 | 7.41 | 11.3863 | YES | 869
2 / 16:00 | 0.75 | 111 | 83.25 | 19.8 | 7.21 | 10.3648 | YES | 850
3 / 8:00 | 0.75 | 111 | 83.25 | 19.3 | 7.33 | 11.2134 | YES | 836
4 / 16:00 | 0.74 | 111 | 82.14 | 19.2 | 7.41 | 11.6185 | YES | 807
5 / 8:00 | 0.71 | 111 | 78.81 | 19.2 | 7.36 | 11.3641 | YES | 792
6 / 8:00 | 0.72 | 111 | 79.92 | 19.2 | 7.38 | 11.4626 | YES | 787
7 / 8:00 | 0.72 | 111 | 79.92 | 19.2 | 7.44 | 11.7225 | YES | 857
8 / 16:00 | 0.68 | 111 | 75.48 | 19.2 | 7.45 | 11.7125 | YES | 878
9 / 8:00 | 0.69 | 111 | 76.59 | 19.1 | 7.47 | 11.8936 | YES | 825
10 / 8:00 | 0.72 | 111 | 79.92 | 19.2 | 7.39 | 11.5055 | YES | 842
11 / 8:00 | 0.73 | 111 | 81.03 | 18.9 | 7.36 | 11.6226 | YES | 825
12 / 8:00 | 0.75 | 111 | 83.25 | 18.4 | 7.35 | 12.0028 | YES | 823
13 / 8:00 | 0.76 | 111 | 84.36 | 18.4 | 7.37 | 12.1066 | YES | 858
14 / 8:00 | 0.77 | 111 | 85.47 | 18.6 | 7.41 | 12.1386 | YES | 887
15 / 4:00 | 0.75 | 111 | 83.25 | 18.5 | 7.41 | 12.1924 | YES | 904
16 / 20:00 | 0.75 | 111 | 83.25 | 18.4 | 7.32 | 11.8691 | YES | 870
17 / 8:00 | 0.76 | 111 | 84.36 | 18.4 | 7.37 | 12.1066 | YES | 847
18 / 8:00 | 0.74 | 111 | 82.14 | 18.1 | 7.36 | 12.2789 | YES | 835
19 / 8:00 | 0.72 | 111 | 79.92 | 17.9 | 7.4 | 12.6029 | YES | 835
20 / 16:00 | 0.77 | 111 | 85.47 | 17.7 | 7.24 | 12.1026 | YES | 817
21 / 8:00 | 0.78 | 111 | 86.58 | 17.6 | 7.2 | 12.0174 | YES | 883
22 / 8:00 | 0.75 | 111 | 83.25 | 17.8 | 7.33 | 12.4035 | YES | 886
23 / 8:00 | 0.75 | 111 | 83.25 | 17.6 | 7.4 | 12.9034 | YES | 890
24 / 8:00 | 0.75 | 111 | 83.25 | 17.6 | 7.34 | 12.6181 | YES | 886
25 / 8:00 | 0.76 | 111 | 84.36 | 17.6 | 7.31 | 12.4921 | YES | 819
26/ 24:00 | 0.77 | 111 | 85.47 | 17.4 | 7.38 | 13.0103 | YES | 815
27 / 8:00 | 0.74 | 111 | 82.14 | 17.5 | 7.35 | 12.7359 | YES | 837
28 / 24:00 | 0.74 | 111 | 82.14 | 17.3 | 7.33 | 12.8121 | YES | 813
29 / 12:00 | 0.74 | 111 | 82.14 | 17.5 | 7.41 | 13.0237 | YES | 1027
30 / 8:00 | 0.7 | 111 | 77.7 | 17.1 | 7.35 | 13.0224 | YES | 873
31 |  | 111 |  |  |  |  | NO
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Sep | 0.028361 | 999.99 | 0.034367 | 999.99 | 999.99 | 0.029264 | 8 | 0 | 0.034721 | 0.73373 | 999.99 | 0.74562 | 999.99 | 999.99 | 0.75375 | 0 | 0.74562 | 0.75
2 | Sep | 999.99 | 0.031423 | 999.99 | 999.99 | 0.032051 | 0.029225 | 16 | 0 | 0.035388 | 999.99 | 0.76629 | 999.99 | 999.99 | 0.74839 | 0.77772 | 16 | 0.74839 | 0.75
3 | Sep | 999.99 | 999.99 | 0.036016 | 0.038764 | 999.99 | 999.99 | 12 | 0 | 0.038882 | 999.99 | 999.99 | 0.74021 | 0.77165 | 999.99 | 999.99 | 8 | 0.74021 | 0.74
4 | Sep | 0.035506 | 0.045477 | 0.036232 | 999.99 | 0.036625 | 999.99 | 4 | 0 | 0.045477 | 0.75157 | 0.74115 | 0.76152 | 999.99 | 0.7332 | 999.99 | 16 | 0.7332 | 0.73
5 | Sep | 0.037567 | 999.99 | 0.037233 | 0.037999 | 999.99 | 999.99 | 12 | 0 | 0.038136 | 0.71082 | 999.99 | 0.70576 | 0.74397 | 999.99 | 999.99 | 8 | 0.70576 | 0.71
6 | Sep | 0.036154 | 999.99 | 0.033602 | 0.03739 | 0.03213 | 999.99 | 12 | 0 | 0.03739 | 0.73903 | 999.99 | 0.72796 | 0.76188 | 0.77359 | 999.99 | 8 | 0.72796 | 0.73
7 | Sep | 0.038018 | 999.99 | 0.035349 | 0.036939 | 0.039314 | 0.03847 | 20 | 0 | 0.039471 | 0.74368 | 999.99 | 0.71965 | 0.73202 | 0.73173 | 0.7488 | 8 | 0.71965 | 0.72
8 | Sep | 999.99 | 999.99 | 0.050031 | 0.057451 | 0.046439 | 0.03054 | 12 | 0 | 0.13483 | 999.99 | 999.99 | 0.68974 | 0.67596 | 0.68185 | 0.69698 | 16 | 0.67596 | 0.68
9 | Sep | 999.99 | 999.99 | 0.031403 | 0.03423 | 0.029833 | 999.99 | 12 | 0 | 0.034524 | 999.99 | 999.99 | 0.68662 | 0.73414 | 0.74156 | 999.99 | 8 | 0.68662 | 0.69
10 | Sep | 999.99 | 999.99 | 0.028341 | 0.023238 | 0.021844 | 999.99 | 8 | 0 | 0.031894 | 999.99 | 999.99 | 0.72201 | 0.78054 | 0.78808 | 999.99 | 8 | 0.72201 | 0.72
11 | Sep | 0.027478 | 999.99 | 0.068659 | 0.022767 | 999.99 | 999.99 | 8 | 0 | 0.068699 | 0.75027 | 999.99 | 0.74344 | 0.76476 | 999.99 | 999.99 | 8 | 0.74344 | 0.74
12 | Sep | 0.024926 | 999.99 | 0.023041 | 0.022452 | 999.99 | 0.024985 | 0 | 0 | 0.027497 | 0.75157 | 999.99 | 0.74886 | 0.7819 | 999.99 | 0.75446 | 8 | 0.74886 | 0.75
13 | Sep | 999.99 | 999.99 | 0.026123 | 0.037665 | 999.99 | 999.99 | 12 | 0 | 0.037744 | 999.99 | 999.99 | 0.76264 | 0.79344 | 999.99 | 999.99 | 8 | 0.76264 | 0.76
14 | Sep | 999.99 | 999.99 | 0.025789 | 0.025358 | 0.027458 | 999.99 | 16 | 0 | 0.027674 | 999.99 | 999.99 | 0.76812 | 0.78732 | 0.79738 | 999.99 | 8 | 0.76812 | 0.77
15 | Sep | 999.99 | 0.024199 | 0.024337 | 0.023022 | 999.99 | 0.025907 | 4 | 0 | 0.027772 | 999.99 | 0.75027 | 0.77253 | 0.78708 | 999.99 | 0.75186 | 4 | 0.75027 | 0.75
16 | Sep | 999.99 | 999.99 | 0.024729 | 0.023787 | 999.99 | 0.026005 | 20 | 0 | 0.028243 | 999.99 | 999.99 | 0.76046 | 0.77754 | 999.99 | 0.75281 | 20 | 0.75281 | 0.75
17 | Sep | 999.99 | 999.99 | 0.028322 | 0.051543 | 0.026692 | 999.99 | 12 | 0 | 0.051661 | 999.99 | 999.99 | 0.75917 | 0.79297 | 0.78437 | 999.99 | 8 | 0.75917 | 0.76
18 | Sep | 0.028891 | 999.99 | 0.026614 | 0.064086 | 999.99 | 0.046243 | 12 | 0 | 0.064086 | 0.76547 | 999.99 | 0.74227 | 0.77142 | 999.99 | 0.74698 | 8 | 0.74227 | 0.74
19 | Sep | 999.99 | 999.99 | 0.025652 | 0.027811 | 0.027026 | 999.99 | 12 | 0 | 0.028655 | 999.99 | 999.99 | 0.73155 | 0.77053 | 0.79191 | 999.99 | 8 | 0.73155 | 0.73
20 | Sep | 0.023571 | 999.99 | 0.024965 | 0.36231 | 0.031148 | 0.02683 | 12 | 0 | 0.40659 | 0.77813 | 999.99 | 0.78149 | 0.77077 | 0.76877 | 0.80569 | 16 | 0.76877 | 0.77
21 | Sep | 0.025475 | 999.99 | 0.027065 | 0.027478 | 0.027046 | 999.99 | 12 | 0 | 0.030815 | 0.81152 | 999.99 | 0.7766 | 0.78655 | 0.7915 | 999.99 | 8 | 0.7766 | 0.78
22 | Sep | 0.026025 | 999.99 | 0.025672 | -0.0016324 | 999.99 | 999.99 | 0 | 0 | 0.028636 | 0.7534 | 999.99 | 0.76264 | 0.78655 | 999.99 | 999.99 | 8 | 0.76264 | 0.76
23 | Sep | -0.0014754 | 999.99 | 0.00017343 | 0.0021756 | -0.0016324 | 999.99 | 0 | 0 | 0.0022345 | 0.76818 | 999.99 | 0.75675 | 0.77289 | 0.78143 | 999.99 | 8 | 0.75675 | 0.76
24 | Sep | 0.0021363 | 999.99 | 0.00035007 | 0.025259 | 999.99 | 0.030029 | 20 | 0 | 0.031129 | 0.75628 | 999.99 | 0.75004 | 0.78355 | 999.99 | 0.76776 | 8 | 0.75004 | 0.75
25 | Sep | 999.99 | 999.99 | 0.024474 | 0.038215 | 0.025574 | 999.99 | 12 | 0 | 0.038352 | 999.99 | 999.99 | 0.7554 | 0.7746 | 0.78949 | 999.99 | 8 | 0.7554 | 0.76
26 | Sep | 0.025731 | 0.030599 | 0.027006 | 999.99 | 999.99 | 0.027517 | 4 | 0 | 0.030697 | 0.77018 | 0.76441 | 0.7889 | 999.99 | 999.99 | 0.76918 | 4 | 0.76441 | 0.76
27 | Sep | 999.99 | 999.99 | 0.14884 | 0.027674 | 999.99 | 999.99 | 8 | 0 | 0.14886 | 999.99 | 999.99 | 0.73897 | 0.76246 | 999.99 | 999.99 | 8 | 0.73897 | 0.74
28 | Sep | 0.029166 | 999.99 | 0.027438 | 0.026516 | 0.030108 | 999.99 | 16 | 0 | 0.03052 | 0.74097 | 999.99 | 0.73231 | 0.76894 | 0.78143 | 999.99 | 24 | 0.74 | 0.74
29 | Sep | 999.99 | 999.99 | 999.99 | 0.030088 | 0.028812 | 0.032247 | 20 | 0 | 0.033091 | 999.99 | 999.99 | 999.99 | 0.72925 | 0.75139 | 0.75063 | 12 | 0.72925 | 0.73
30 | Sep | 999.99 | 999.99 | 0.061986 | 0.033327 | 0.032777 | 0.030285 | 8 | 0 | 0.061986 | 999.99 | 999.99 | 0.70752 | 0.72065 | 0.72189 | 0.76747 | 8 | 0.70752 | 0.71