## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | Oct_22
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
2 | 0.02 | OFF | OFF | 0.02 | 0.03 | OFF | 0.03
3 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
4 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
5 | OFF | 0.02 | 0.02 | 0.021118 | OFF | OFF | 0.02
6 | 0.020548 | OFF | 0.023669 | 0.019626 | 0.023238 | OFF | 0.024062
7 | OFF | 0.024062 | 0.023728 | 0.024023 | OFF | OFF | 0.02
8 | 0.023002 | OFF | 0.02 | 0.019763 | OFF | OFF | 0.02
9 | 0.024749 | OFF | OFF | 0.018958 | OFF | OFF | 0.024749
10 | 0.020725 | OFF | 0.021334 | 0.023159 | OFF | OFF | 0.024298
11 | 0.02 | OFF | 0.024847 | 0.02 | OFF | 0.024101 | 0.02
12 | 0.024729 | OFF | 0.021746 | 0.02153 | OFF | OFF | 0.02
13 | OFF | OFF | 0.022276 | OFF | 0.020764 | OFF | 0.024808
14 | 0.02 | OFF | 0.023827 | OFF | OFF | 0.023218 | 0.024671
15 | OFF | OFF | 0.023591 | 0.022217 | OFF | OFF | 0.023591
16 | 0.021569 | OFF | 0.021373 | 0.021491 | OFF | OFF | 0.024671
17 | 0.022982 | OFF | 0.022138 | OFF | 0.024003 | 0.02 | 0.02
18 | OFF | OFF | 0.021844 | 0.022119 | 0.02 | OFF | 0.02
19 | OFF | 0.02 | OFF | OFF | 0.02 | OFF | 0.02
20 | OFF | OFF | 0.02 | OFF | 0.02 | 0.02 | 0.02
21 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
22 | 0.02 | OFF | 0.02 | 0.022767 | 0.022865 | OFF | 0.02
23 | 0.02 | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
24 | 0.02 | OFF | 0.02 | 0.024062 | OFF | OFF | 0.02
25 | 0.02 | OFF | 0.024121 | 0.02 | OFF | OFF | 0.02
26 | OFF | 0.02 | OFF | 0.023297 | 0.02 | OFF | 0.02
27 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
28 | OFF | OFF | 0.02 | 0.022158 | OFF | 0.02155 | 0.02
29 | OFF | OFF | 0.02 | 0.024062 | 0.023277 | 0.022001 | 0.02
30 | OFF | OFF | 0.023807 | 0.02 | 0.031796 | OFF | 0.032404
31 | OFF | OFF | 0.022394 | 0.021844 | OFF | OFF | 0.02418
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J. Dues
[5 empty] | SIGNATURE:Zachary J. Dues |  |  | DATE:11/01/2022
[5 empty] | PHONE #: (541) 336-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | Oct_22 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 8:00 | 0.72 | 111 | 79.92 | 17 | 7.32 | 12.994 | YES | 895
2/24:00 | 0.73 | 111 | 81.03 | 17.4 | 7.33 | 12.7119 | YES | 808
3 / 12:00 | 0.76 | 111 | 84.36 | 17.3 | 7.18 | 12.1431 | YES | 776
4 / 8:00 | 0.69 | 111 | 76.59 | 17.2 | 7.08 | 11.6827 | YES | 817
5 / 4:00 | 0.69 | 111 | 76.59 | 17 | 7.21 | 12.4295 | YES | 833
6 / 24:00 | 0.7 | 111 | 77.7 | 16.9 | 7.24 | 12.6684 | YES | 865
7 / 4:00 | 0.76 | 111 | 84.36 | 16.8 | 7.29 | 13.0829 | YES | 902
8 / 24:00 | 0.76 | 111 | 84.36 | 16.8 | 7.29 | 13.0829 | YES | 906
9 / 24:00 | 0.78 | 111 | 86.58 | 16.9 | 7.34 | 13.27 | YES | 858
10 / 8:00 | 0.78 | 111 | 86.58 | 16.9 | 7.37 | 13.4189 | YES | 916
11 / 12:00 | 0.75 | 111 | 83.25 | 16.6 | 7.32 | 13.393 | YES | 812
12 / 8:00 | 0.75 | 111 | 83.25 | 16.5 | 7.26 | 13.1853 | YES | 827
13 / 8:00 | 0.75 | 111 | 83.25 | 16.5 | 7.18 | 12.7983 | YES | 829
14 / 24:00 | 0.76 | 111 | 84.36 | 16.5 | 7.25 | 13.1514 | YES | 828
15 / 8:00 | 0.77 | 111 | 85.47 | 16.2 | 7.35 | 13.9425 | YES | 919
16 / 8:00 | 0.76 | 111 | 84.36 | 16 | 7.38 | 14.2723 | YES | 861
17 / 8:00 | 0.77 | 111 | 85.47 | 15.8 | 7.31 | 14.1094 | YES | 865
18 / 8:00 | 0.78 | 111 | 86.58 | 15.3 | 7.41 | 15.1575 | YES | 827
19 / 4:00 | 0.78 | 111 | 86.58 | 15.3 | 7.4 | 15.1014 | YES | 832
20 / 16:00 | 0.78 | 111 | 86.58 | 15.3 | 7.42 | 15.2138 | YES | 824
21 / 8:00 | 0.78 | 111 | 86.58 | 15.2 | 7.41 | 15.259 | YES | 835
22 / 8:00 | 0.77 | 111 | 85.47 | 14.9 | 7.38 | 15.3779 | YES | 888
23 / 8:00 | 0.76 | 111 | 84.36 | 14.3 | 7.37 | 15.9284 | YES | 883
24 / 12:00 | 0.75 | 111 | 83.25 | 14.3 | 7.32 | 15.6184 | YES | 887
25 / 8:00 | 0.69 | 111 | 76.59 | 14.1 | 7.4 | 16.1929 | YES | 862
26 / 4:00 | 0.65 | 111 | 72.15 | 13.9 | 7.24 | 15.3959 | YES | 836
27 / 8:00 | 0.66 | 111 | 73.26 | 13.6 | 7.34 | 16.3181 | YES | 851
28 / 8:00 | 0.71 | 111 | 78.81 | 13.5 | 7.1 | 15.1159 | YES | 907
29 / 20:00 | 0.79 | 111 | 87.69 | 13.2 | 7.13 | 15.7366 | YES | 880
30 / 8:00 | 0.75 | 111 | 83.25 | 13 | 7.28 | 16.7815 | YES | 857
31 / 8:00 | 0.76 | 111 | 84.36 | 12.9 | 7.34 | 17.2921 | YES | 834
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | Oct | 999.99 | 999.99 | 0.031639 | 0.031973 | 999.99 | 999.99 | 8 | 0 | 0.033366 | 999.99 | 999.99 | 0.713 | 0.75157 | 999.99 | 999.99 | 8 | 0.713 | 0.71
2 | Oct | 0.029362 | 999.99 | 999.99 | 0.029068 | 0.03686 | 999.99 | 16 | 0 | 0.038175 | 0.72313 | 999.99 | 999.99 | 0.73838 | 0.80757 | 999.99 | 12 | 0.73838 | 0.74
3 | Oct | 999.99 | 999.99 | 0.032071 | 0.030383 | 999.99 | 999.99 | 12 | 0 | 0.034093 | 999.99 | 999.99 | 0.7458 | 0.76411 | 999.99 | 999.99 | 12 | 0.7458 | 0.75
4 | Oct | 999.99 | 999.99 | 0.033229 | 0.029813 | 999.99 | 999.99 | 8 | 0 | 0.033229 | 999.99 | 999.99 | 0.69156 | 0.7405 | 999.99 | 999.99 | 8 | 0.69156 | 0.69
5 | Oct | 999.99 | 0.029715 | 0.025515 | 0.021118 | 999.99 | 999.99 | 4 | 0 | 0.036036 | 999.99 | 0.68797 | 0.70764 | 0.74886 | 999.99 | 999.99 | 4 | 0.68797 | 0.69
6 | Oct | 0.020548 | 999.99 | 0.023669 | 0.019626 | 0.023238 | 999.99 | 16 | 0 | 0.024062 | 0.70322 | 999.99 | 0.7193 | 0.76423 | 0.78284 | 999.99 | 24 | 0.7193 | 0.72
7 | Oct | 999.99 | 0.024062 | 0.023728 | 0.024023 | 999.99 | 999.99 | 8 | 0 | 0.027497 | 999.99 | 0.75675 | 0.76429 | 0.7995 | 999.99 | 999.99 | 4 | 0.75675 | 0.76
8 | Oct | 0.023002 | 999.99 | 0.030186 | 0.019763 | 999.99 | 999.99 | 8 | 0 | 0.03264 | 0.76847 | 999.99 | 0.76517 | 0.80286 | 999.99 | 999.99 | 8 | 0.76517 | 0.77
9 | Oct | 0.024749 | 999.99 | 999.99 | 0.018958 | 999.99 | 999.99 | 0 | 0 | 0.024749 | 0.77077 | 999.99 | 999.99 | 0.79462 | 999.99 | 999.99 | 24 | 0.78 | 0.78
10 | Oct | 0.020725 | 999.99 | 0.021334 | 0.023159 | 999.99 | 999.99 | 0 | 0 | 0.024298 | 0.78855 | 999.99 | 0.78172 | 0.80716 | 999.99 | 999.99 | 8 | 0.78172 | 0.78
11 | Oct | 0.021942 | 999.99 | 0.024847 | 0.026496 | 999.99 | 0.024101 | 12 | 0 | 0.028008 | 0.76706 | 999.99 | 0.74391 | 0.76453 | 999.99 | 0.77212 | 12 | 0.74391 | 0.74
12 | Oct | 0.024729 | 999.99 | 0.021746 | 0.02153 | 999.99 | 999.99 | 8 | 0 | 0.025672 | 0.77495 | 999.99 | 0.74338 | 0.77695 | 999.99 | 999.99 | 8 | 0.74338 | 0.74
13 | Oct | 999.99 | 999.99 | 0.022276 | 999.99 | 0.020764 | 999.99 | 16 | 0 | 0.024808 | 999.99 | 999.99 | 0.76117 | 999.99 | 0.76152 | 999.99 | 8 | 0.76117 | 0.76
14 | Oct | 0.031698 | 999.99 | 0.023827 | 999.99 | 999.99 | 0.023218 | 8 | 0 | 0.024671 | 0.74969 | 999.99 | 0.77059 | 999.99 | 999.99 | 0.76606 | 20 | 0.76606 | 0.77
15 | Oct | 999.99 | 999.99 | 0.023591 | 0.022217 | 999.99 | 999.99 | 8 | 0 | 0.023591 | 999.99 | 999.99 | 0.76947 | 0.80492 | 999.99 | 999.99 | 8 | 0.76947 | 0.77
16 | Oct | 0.021569 | 999.99 | 0.021373 | 0.021491 | 999.99 | 999.99 | 0 | 0 | 0.024671 | 0.77336 | 999.99 | 0.769 | 0.80157 | 999.99 | 999.99 | 8 | 0.769 | 0.77
17 | Oct | 0.022982 | 999.99 | 0.022138 | 999.99 | 0.024003 | 0.026457 | 20 | 0 | 0.026555 | 0.76252 | 999.99 | 0.76258 | 999.99 | 0.78855 | 0.80804 | 8 | 0.76258 | 0.76
18 | Oct | 999.99 | 999.99 | 0.021844 | 0.022119 | 0.026908 | 999.99 | 16 | 0 | 0.026908 | 999.99 | 999.99 | 0.78537 | 0.82312 | 0.82023 | 999.99 | 8 | 0.78537 | 0.79
19 | Oct | 999.99 | 0.025456 | 999.99 | 999.99 | 0.026516 | 999.99 | 8 | 0 | 0.040138 | 999.99 | 0.79238 | 999.99 | 999.99 | 0.80439 | 999.99 | 4 | 0.79238 | 0.79
20 | Oct | 999.99 | 999.99 | 0.026476 | 999.99 | 0.025986 | 0.022531 | 8 | 0 | 0.026535 | 999.99 | 999.99 | 0.78337 | 999.99 | 0.79256 | 0.81564 | 16 | 0.78337 | 0.78
21 | Oct | 999.99 | 999.99 | 0.026005 | 0.025259 | 999.99 | 999.99 | 8 | 0 | 0.026633 | 999.99 | 999.99 | 0.77471 | 0.82059 | 999.99 | 999.99 | 8 | 0.77471 | 0.77
22 | Oct | 0.029225 | 999.99 | 0.022747 | 0.022767 | 0.022865 | 999.99 | 8 | 0 | 0.026575 | 0.78849 | 999.99 | 0.76447 | 0.78802 | 0.81417 | 999.99 | 8 | 0.76447 | 0.76
23 | Oct | 0.029087 | 999.99 | 0.025436 | 0.023728 | 999.99 | 999.99 | 12 | 0 | 0.025593 | 0.77772 | 999.99 | 0.76023 | 0.79155 | 999.99 | 999.99 | 8 | 0.76023 | 0.76
24 | Oct | 0.026594 | 999.99 | 0.027536 | 0.024062 | 999.99 | 999.99 | 8 | 0 | 0.027792 | 0.76718 | 999.99 | 0.75175 | 0.76182 | 999.99 | 999.99 | 12 | 0.75175 | 0.75
25 | Oct | 0.025004 | 999.99 | 0.024121 | 0.025181 | 999.99 | 999.99 | 0 | 0 | 0.028793 | 0.70793 | 999.99 | 0.69769 | 0.72383 | 999.99 | 999.99 | 8 | 0.69769 | 0.7
26 | Oct | 999.99 | 0.030186 | 999.99 | 0.023297 | 0.028361 | 999.99 | 4 | 0 | 0.030795 | 999.99 | 0.66224 | 999.99 | 0.6961 | 0.717 | 999.99 | 4 | 0.66224 | 0.66
27 | Oct | 999.99 | 999.99 | 0.028282 | 0.047126 | 0.029166 | 999.99 | 12 | 0 | 0.048402 | 999.99 | 999.99 | 0.65217 | 0.68191 | 0.67572 | 999.99 | 8 | 0.65217 | 0.65
28 | Oct | 999.99 | 999.99 | 0.027046 | 0.022158 | 999.99 | 0.02155 | 8 | 0 | 0.027438 | 999.99 | 999.99 | 0.70087 | 0.79102 | 999.99 | 0.75186 | 8 | 0.70087 | 0.7
29 | Oct | 999.99 | 999.99 | 0.029146 | 0.024062 | 0.023277 | 0.022001 | 8 | 0 | 0.031187 | 999.99 | 999.99 | 0.83537 | 0.81105 | 0.78961 | 0.79097 | 16 | 0.78961 | 0.79
30 | Oct | 999.99 | 999.99 | 0.023807 | 0.025161 | 0.031796 | 999.99 | 16 | 0 | 0.032404 | 999.99 | 999.99 | 0.74533 | 0.81158 | 0.79574 | 999.99 | 8 | 0.74533 | 0.75
31 | Oct | 999.99 | 999.99 | 0.022394 | 0.021844 | 999.99 | 999.99 | 8 | 0 | 0.02418 | 999.99 | 999.99 | 0.75793 | 0.78531 | 999.99 | 999.99 | 8 | 0.75793 | 0.76