## Report
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lincoln
Conventional or Direct Filtration | [6 empty] | Month/Year: | May_23
System Name: | Toledo Water Utilities |  |  | ID#: 41 00899 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
3 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
4 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
5 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
6 | OFF | OFF | 0.03 | 0.02 | 0.02 | OFF | 0.03
7 | OFF | OFF | OFF | 0.04 | 0.02 | 0.02 | 0.04
8 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
9 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
10 | OFF | OFF | 0.03 | 0.02 | 0.02 | OFF | 0.03
11 | OFF | OFF | 0.03 | 0.04 | 0.03 | OFF | 0.04
12 | OFF | OFF | 0.03 | OFF | 0.03 | 0.02 | 0.03
13 | OFF | OFF | 0.062025 | 0.02 | 0.02 | 0.02 | 0.06
14 | OFF | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02
15 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
16 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
17 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
18 | OFF | 0.02 | 0.02 | 0.02 | 0.02 | OFF | 0.02
19 | OFF | OFF | 0.02 | 0.02 | OFF | 0.02 | 0.02
20 | OFF | OFF | 0.03 | 0.02 | 0.02 | OFF | 0.03
21 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
22 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
23 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
24 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
25 | OFF | OFF | 0.02 | OFF | OFF | 0.02 | 0.02
26 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
27 | OFF | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.05
28 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
29 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
30 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
31 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Zachary J. Dues
[5 empty] | SIGNATURE:Zachary J. Dues |  |  | DATE:06/01/2023
[5 empty] | PHONE #: (541)366-2610 |  |  | CERT #:269781
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : | A
System Name: | Toledo Water Utilities |  | ID#: 41 00899 |  | Month/Year: | May_23 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 / 8:00 | 0.68 | 111 | 75.48 | 10.8 | 7.47 | 20.8092 | YES | 796
2 / 8:00 | 0.7 | 111 | 77.7 | 10.6 | 7.38 | 20.4774 | YES | 850
3 / 12:00 | 0.73 | 111 | 81.03 | 10.4 | 7.32 | 20.386 | YES | 828
4 / 8:00 | 0.74 | 111 | 82.14 | 10.7 | 7.35 | 20.2227 | YES | 817
5 / 8:00 | 0.71 | 111 | 78.81 | 10.5 | 7.3 | 20.0677 | YES | 815
6 / 12:00 | 0.65 | 111 | 72.15 | 10.1 | 7.35 | 20.8217 | YES | 834
7 / 16:00 | 0.72 | 111 | 79.92 | 10.6 | 7.38 | 20.5234 | YES | 795
8 / 8:00 | 0.7 | 111 | 77.7 | 10.7 | 7.22 | 19.2442 | YES | 797
9 / 8:00 | 0.68 | 111 | 75.48 | 10.6 | 7.2 | 19.1932 | YES | 750
10 / 8:00 | 0.67 | 111 | 74.37 | 11 | 7.27 | 19.1383 | YES | 782
11 / 8:00 | 0.72 | 111 | 79.92 | 11.3 | 7.59 | 21.0951 | YES | 821
12 / 16:00 | 0.7 | 111 | 77.7 | 11.7 | 7.2 | 17.9152 | YES | 863
13 / 8:00 | 0.69 | 111 | 76.59 | 12 | 7.27 | 17.9798 | YES | 862
14 / 12:00 | 0.77 | 111 | 85.47 | 13 | 7.4 | 17.5824 | YES | 851
15 / 8:00 | 0.76 | 111 | 84.36 | 14.5 | 7.52 | 16.6147 | YES | 850
16 / 16:00 | 0.71 | 111 | 78.81 | 14.7 | 7.62 | 16.9161 | YES | 844
17 / 8:00 | 0.71 | 111 | 78.81 | 15.3 | 7.72 | 16.8659 | YES | 823
18 / 4:00 | 0.7 | 111 | 77.7 | 15.5 | 7.78 | 16.9969 | YES | 816
19 / 20:00 | 0.68 | 111 | 75.48 | 15.5 | 7.63 | 16.0429 | YES | 823
20 / 8:00 | 0.66 | 111 | 73.26 | 15.8 | 7.59 | 15.4586 | YES | 825
21 / 8:00 | 0.7 | 111 | 77.7 | 15.8 | 7.61 | 15.6447 | YES | 922
22 / 8:00 | 0.72 | 111 | 79.92 | 15.8 | 7.6 | 15.6224 | YES | 949
23 / 8:00 | 0.72 | 111 | 79.92 | 15.7 | 7.4 | 14.6031 | YES | 896
24 / 8:00 | 0.74 | 111 | 82.14 | 15.4 | 7.16 | 13.6595 | YES | 899
25 / 8:00 | 0.74 | 111 | 82.14 | 14.8 | 7.4 | 15.5428 | YES | 909
26 / 8:00 | 0.74 | 111 | 82.14 | 14.9 | 7.67 | 17.0619 | YES | 814
27 / 12:00 | 0.74 | 111 | 82.14 | 15 | 7.75 | 17.4573 | YES | 849
28 / 12:00 | 0.73 | 111 | 81.03 | 15 | 7.67 | 16.9295 | YES | 849
29 / 8:00 | 0.69 | 111 | 76.59 | 15.4 | 7.53 | 15.5808 | YES | 783
30 / 8:00 | 0.71 | 111 | 78.81 | 15.8 | 7.47 | 14.8705 | YES | 810
31 / 8:00 | 0.72 | 111 | 79.92 | 15.8 | 7.45 | 14.7775 | YES | 880
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## DATA_1
DAY | MONTH | TURB 12 AM [NTU] | TURB 4 AM [NTU] | TURB 8 AM [NTU] | TURB NOON [NTU] | TURB 4 PM [NTU] | TURB 8 PM [NTU] | TURB HIGHEST DAILY [HOUR] | TURB HIGHEST DAILY [MIN] | TURB HIGHEST DAILY [NTU] | CHLOR 12 AM [ppm] | CHLOR 4 AM [ppm] | CHLOR 8 AM [ppm] | CHLOR NOON [ppm] | CHLOR 4 PM [ppm] | CHLOR 8 PM [ppm] | CHLOR LOWEST DAILY [HOUR] | CHLOR LOWEST DAILY [ppm] | CHLOR LOWEST DAILY (Rounded)
1 | May | 999.99 | 999.99 | 0.053231 | 0.051111 | 0.063929 | 999.99 | 16 | 0 | 0.064047 | 999.99 | 999.99 | 0.67937 | 0.70434 | 0.7309 | 999.99 | 8 | 0.67937 | 0.68
2 | May | 999.99 | 999.99 | 0.058236 | 0.061632 | 0.059728 | 999.99 | 12 | 0 | 0.062908 | 999.99 | 999.99 | 0.70994 | 0.73473 | 0.74144 | 999.99 | 8 | 0.70994 | 0.71
3 | May | 999.99 | 999.99 | 999.99 | 0.056607 | 0.058413 | 999.99 | 12 | 0 | 0.060886 | 999.99 | 999.99 | 999.99 | 0.73337 | 0.78573 | 999.99 | 12 | 0.73337 | 0.73
4 | May | 999.99 | 999.99 | 0.056745 | 0.060121 | 0.057432 | 999.99 | 16 | 0 | 0.060847 | 999.99 | 999.99 | 0.74415 | 0.74727 | 0.75652 | 999.99 | 8 | 0.74415 | 0.74
5 | May | 999.99 | 999.99 | 0.058668 | 0.057157 | 0.060788 | 999.99 | 16 | 0 | 0.060945 | 999.99 | 999.99 | 0.70422 | 0.73196 | 0.72595 | 999.99 | 8 | 0.70422 | 0.7
6 | May | 999.99 | 999.99 | 0.061456 | 0.056156 | 0.06122 | 999.99 | 12 | 0 | 0.13601 | 999.99 | 999.99 | 0.68562 | 0.66124 | 0.72089 | 999.99 | 12 | 0.66124 | 0.66
7 | May | 999.99 | 999.99 | 999.99 | 0.046714 | 0.044908 | 0.042749 | 12 | 0 | 0.051131 | 999.99 | 999.99 | 999.99 | 0.71983 | 0.72266 | 0.72766 | 16 | 0.71983 | 0.72
8 | May | 999.99 | 999.99 | 0.037685 | 0.039883 | 0.044869 | 999.99 | 16 | 0 | 0.044869 | 999.99 | 999.99 | 0.6938 | 0.70735 | 0.71312 | 999.99 | 8 | 0.7 | 0.7
9 | May | 999.99 | 999.99 | 0.03898 | 0.039844 | 0.040217 | 999.99 | 12 | 0 | 0.042376 | 999.99 | 999.99 | 0.68191 | 0.68073 | 0.70705 | 999.99 | 8 | 0.68073 | 0.68
10 | May | 999.99 | 999.99 | 0.04163 | 0.044614 | 0.045733 | 999.99 | 16 | 0 | 0.046047 | 999.99 | 999.99 | 0.67307 | 0.71848 | 0.73832 | 999.99 | 8 | 0.67307 | 0.67
11 | May | 999.99 | 999.99 | 0.052269 | 0.054919 | 0.056018 | 999.99 | 16 | 0 | 0.056038 | 999.99 | 999.99 | 0.7153 | 0.73414 | 0.72866 | 999.99 | 8 | 0.7153 | 0.72
12 | May | 999.99 | 999.99 | 0.057314 | 999.99 | 0.059512 | 0.058178 | 20 | 0 | 0.05965 | 999.99 | 999.99 | 0.70069 | 999.99 | 0.69522 | 0.71877 | 16 | 0.69522 | 0.7
13 | May | 999.99 | 999.99 | 0.062025 | 0.059512 | 0.063458 | 0.063909 | 20 | 0 | 0.065244 | 999.99 | 999.99 | 0.68803 | 0.72054 | 0.74957 | 0.77642 | 8 | 0.68803 | 0.69
14 | May | 999.99 | 999.99 | 999.99 | 0.069641 | 0.071054 | 0.070132 | 16 | 0 | 0.072075 | 999.99 | 999.99 | 999.99 | 0.77689 | 0.79161 | 0.79839 | 12 | 0.77689 | 0.78
15 | May | 999.99 | 999.99 | 0.076354 | 0.076079 | 0.075922 | 999.99 | 16 | 0 | 0.081477 | 999.99 | 999.99 | 0.76788 | 0.7786 | 0.78037 | 999.99 | 8 | 0.76788 | 0.77
16 | May | 999.99 | 999.99 | 0.081752 | 0.084539 | 0.084638 | 999.99 | 16 | 0 | 0.086915 | 999.99 | 999.99 | 0.7478 | 0.74244 | 0.75699 | 999.99 | 16 | 0.71 | 0.71
17 | May | 999.99 | 999.99 | 0.091272 | 0.091645 | 0.093117 | 999.99 | 16 | 0 | 0.096356 | 999.99 | 999.99 | 0.71553 | 0.73962 | 0.73756 | 999.99 | 8 | 0.71553 | 0.72
18 | May | 999.99 | 0.099065 | 0.10244 | 0.10332 | 0.10397 | 999.99 | 16 | 0 | 0.10668 | 999.99 | 0.70299 | 0.71435 | 0.73196 | 0.72401 | 999.99 | 4 | 0.70299 | 0.7
19 | May | 999.99 | 999.99 | 0.11259 | 0.11226 | 999.99 | 0.11569 | 20 | 0 | 0.11632 | 999.99 | 999.99 | 0.68379 | 0.70729 | 999.99 | 0.68391 | 20 | 0.68379 | 0.68
20 | May | 999.99 | 999.99 | 0.11856 | 0.12005 | 0.12507 | 999.99 | 16 | 0 | 0.12545 | 999.99 | 999.99 | 0.66813 | 0.70087 | 0.7163 | 999.99 | 8 | 0.66813 | 0.67
21 | May | 999.99 | 999.99 | 0.12804 | 0.12945 | 0.12945 | 999.99 | 16 | 0 | 0.13314 | 999.99 | 999.99 | 0.69569 | 0.73214 | 0.74586 | 999.99 | 8 | 0.69569 | 0.7
22 | May | 999.99 | 999.99 | 0.15634 | 0.057333 | 1.002 | 999.99 | 16 | 0 | 1.002 | 999.99 | 999.99 | 0.72737 | 0.76123 | 0.76829 | 999.99 | 8 | 0.72737 | 0.73
23 | May | 999.99 | 999.99 | 1.0019 | 0.11135 | 0.043652 | 0.048697 | 8 | 0 | 1.0023 | 999.99 | 999.99 | 0.72831 | 0.74191 | 0.74821 | 0.75116 | 8 | 0.72831 | 0.73
24 | May | 999.99 | 999.99 | 0.074548 | 0.02999 | 0.026908 | 999.99 | 8 | 0 | 0.074705 | 999.99 | 999.99 | 0.7256 | 0.76111 | 0.77654 | 999.99 | 8 | 0.7256 | 0.73
25 | May | 999.99 | 999.99 | 0.058708 | 999.99 | 999.99 | 0.033307 | 8 | 0 | 0.059473 | 999.99 | 999.99 | 0.74615 | 999.99 | 999.99 | 0.75045 | 8 | 0.74615 | 0.75
26 | May | 999.99 | 999.99 | 0.048088 | 0.039255 | 0.033994 | 0.034623 | 8 | 0 | 0.048127 | 999.99 | 999.99 | 0.72531 | 0.74032 | 0.75292 | 0.76288 | 8 | 0.72531 | 0.73
27 | May | 999.99 | 999.99 | 999.99 | 0.043279 | 0.035898 | 0.036684 | 12 | 0 | 0.049874 | 999.99 | 999.99 | 999.99 | 0.73703 | 0.75198 | 0.7617 | 12 | 0.73703 | 0.74
28 | May | 999.99 | 999.99 | 999.99 | 0.039883 | 0.037783 | 999.99 | 12 | 0 | 0.042258 | 999.99 | 999.99 | 999.99 | 0.72148 | 0.73561 | 999.99 | 12 | 0.72148 | 0.72
29 | May | 999.99 | 999.99 | 0.070956 | 0.035683 | 0.044123 | 999.99 | 8 | 0 | 0.072291 | 999.99 | 999.99 | 0.70157 | 0.71588 | 0.72372 | 999.99 | 8 | 0.70157 | 0.7
30 | May | 999.99 | 999.99 | 0.054428 | 0.03476 | 0.037449 | 0.039451 | 8 | 0 | 0.054448 | 999.99 | 999.99 | 0.6991 | 0.72731 | 0.74309 | 0.75063 | 8 | 0.6991 | 0.7
31 | May | 999.99 | 999.99 | 0.060219 | 0.041532 | 0.028734 | 999.99 | 8 | 0 | 0.060219 | 999.99 | 999.99 | 0.72183 | 0.72919 | 0.75434 | 999.99 | 8 | 0.72183 | 0.72