## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Curry
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2021-01-01
System Name: | City of Gold Beach |  |  | ID#: 4101059 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | off | off | off | 0.02 | 0.02 | off | 0.02
2 | off | off | 0.021 | 0.021 | 0.018 | off | 0.021
3 | off | off | off | 0.02 | 0.021 | 0.018 | 0.025
4 | off | off | off | 0.019 | 0.019 | off | 0.02
5 | off | off | 0.018 | 0.019 | 0.02 | off | 0.024
6 | off | off | 0.021 | 0.018 | 0.018 | off | 0.02
7 | off | off | 0.019 | 0.038 | 0.022 | 0.019 | 0.038
8 | off | off | off | 0.019 | 0.019 | off | 0.05
9 | off | off | 0.024 | 0.021 | off | off | 0.03
10 | off | 0.022 | off | off | 0.03 | 0.022 | 0.059
11 | off | off | off | 0.023 | 0.02 | off | 0.05
12 | off | off | off | 0.023 | 0.02 | off | 0.05
13 | off | off | off | 0.022 | 0.041 | 0.035 | 0.069
14 | off | off | off | off | 0.025 | 0.028 | 0.028
15 | 0.071 | off | off | 0.042 | 0.036 | off | 0.071
16 | off | off | off | 0.03 | 0.044 | 0.031 | 0.068
17 | off | off | off | 0.034 | 0.028 | off | 0.039
18 | off | off | off | 0.029 | 0.022 | 0.022 | 0.049
19 | off | off | off | 0.022 | 0.022 | off | 0.049
20 | off | off | 0.022 | 0.02 | off | off | 0.031
21 | off | 0.021 | off | off | 0.033 | 0.022 | 0.05
22 | off | off | off | 0.022 | 0.022 | 0.024 | 0.029
23 | off | off | off | 0.019 | 0.021 | off | 0.024
24 | off | off | off | 0.02 | 0.02 | 0.021 | 0.026
25 | off | off | off | 0.019 | 0.019 | off | 0.023
26 | off | off | 0.019 | 0.02 | 0.02 | off | 0.021
27 | off | off | off | 0.022 | 0.022 | 0.023 | 0.03
28 | off | off | 0.022 | 0.022 | 0.026 | 0.03 | 0.03
29 | 0.03 | 0.031 | 0.031 | 0.033 | 0.035 | 0.03 | 0.045
30 | off | off | off | 0.024 | 0.024 | 0.02 | 0.039
31 | 0.022 | off | off | 0.022 | 0.02 | 0.02 | 0.035
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Will Newdall
[5 empty] | SIGNATURE: |  |  | 2021-02-01
[5 empty] | PHONE #: (541 )247-7459 |  |  | CERT #:FE0054
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | City of Gold Beach |  | ID#: 4101059 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.94 | 60 | 56.4 | 11.8 | 7.17 | 18.0904 | YES | 700
2 | 0.84 | 60 | 50.4 | 11.9 | 7.2 | 17.9611 | YES | 700
3 | 0.82 | 60 | 49.2 | 12.7 | 7.13 | 16.3256 | YES | 700
4 | 1.04 | 60 | 62.4 | 12.4 | 7.16 | 17.5381 | YES | 700
5 | 0.93 | 60 | 55.8 | 12.5 | 7.17 | 17.0024 | YES | 700
6 | 0.92 | 60 | 55.2 | 10.4 | 7.16 | 19.6963 | YES | 700
7 | 0.9 | 60 | 54 | 10.6 | 7.16 | 19.3983 | YES | 700
8 | 0.94 | 60 | 56.4 | 10.6 | 7.14 | 19.3503 | YES | 700
9 | 0.91 | 60 | 54.6 | 10.4 | 7.14 | 19.5383 | YES | 700
10 | 0.81 | 60 | 48.6 | 12.5 | 7.13 | 16.5258 | YES | 700
11 | 0.8 | 60 | 48 | 11.8 | 7.15 | 17.6917 | YES | 700
12 | 0.95 | 60 | 57 | 11.8 | 7.17 | 18.1104 | YES | 700
13 | 0.93 | 60 | 55.8 | 10.4 | 7.11 | 19.3793 | YES | 700
14 | 0.8 | 60 | 48 | 10.9 | 7.2 | 19.0758 | YES | 700
15 | 0.88 | 60 | 52.8 | 12.4 | 7.12 | 16.9995 | YES | 700
16 | 0.9 | 60 | 54 | 11.3 | 7.14 | 18.4103 | YES | 700
17 | 0.77 | 60 | 46.2 | 11.6 | 7.14 | 17.8005 | YES | 700
18 | 0.94 | 60 | 56.4 | 12.1 | 7.08 | 17.2068 | YES | 700
19 | 0.94 | 60 | 56.4 | 11.2 | 7.22 | 19.1332 | YES | 700
20 | 0.88 | 60 | 52.8 | 11 | 7.14 | 18.7294 | YES | 700
21 | 0.95 | 60 | 57 | 13 | 7.14 | 16.3012 | YES | 700
22 | 1.01 | 60 | 60.6 | 11.1 | 7.13 | 18.8137 | YES | 700
23 | 0.94 | 60 | 56.4 | 11.3 | 7.24 | 19.1414 | YES | 700
24 | 0.81 | 60 | 48.6 | 10.9 | 7.17 | 18.9 | YES | 700
25 | 0.93 | 60 | 55.8 | 10.8 | 7.14 | 19.0794 | YES | 700
26 | 0.98 | 60 | 58.8 | 11.3 | 7.19 | 18.8972 | YES | 700
27 | 0.93 | 60 | 55.8 | 11.1 | 7.32 | 19.9154 | YES | 700
28 | 0.93 | 60 | 55.8 | 11.1 | 7.22 | 19.2365 | YES | 700
29 | 0.88 | 60 | 52.8 | 11.1 | 7.25 | 19.3295 | YES | 700
30 | 0.98 | 60 | 58.8 | 10.7 | 7.18 | 19.5803 | YES | 700
31 | 1 | 60 | 60 | 11.3 | 7.2 | 19.0047 | YES | 700
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised September 2016
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2