## EP-A
Water Quality Parameter Form - ENTRY POINT A (EP-A)
Lead & Copper Rule Corrosion Control
PWS Name/ID: |  | Stayton Water Supply - 4100843
Sample Period (Month/Year): |  |  |  | MARCH 2021
Sample Frequency: |  |  | At least every 2 weeks
Day | pH | Alk | Phos | Other | yes/no
1
2
3 | 7.36 | 17 |  |  | YES
4
5
6
7
8
9
10
11
12
13
14
15
16
17 | 7.35 | 19 |  |  | YES
18
19 | [5 empty] | Total excursions during the previous
20 | [5 empty] | five months: ______ | 0
21
22 | [5 empty] | (Over 9 excursions in 6 months is a violation. EP and Dist excurusions are cumulative)
23
24
25
26 | [5 empty] | For OHA use only:
27 | [5 empty] | Minimum Water Quality
28 | [5 empty] | Parameters as set by OHA:
29 | [5 empty] | pH | 7.2
30 | [5 empty] | Alkalinity | 16
31 | 7.37 | 22 |  |  | YES | PO4
Total number of excursions for the month = |  |  |  |  | 0 | Other
Send to dwp.dmce@state.or.us within 10 days after end of the month
[6 empty] | Print Name: | Michael D. Bradley
[6 empty] | Signature: | Michael D. Bradley
[6 empty] | Date: | 2021-03-31
< Have minimums been met for this day?

## DIST
Water Quality Parameter Monitoring Form - DISTRIBUTION
Lead & Copper Rule Corrosion Control
PWS Name/ID: |  | Stayton Water Supply - 4100843
Sample Period (Month/Year): |  | June - September 2021
Required Sample Frequency: |  | Every 3 years
Required # of Sample Locations: |  | 3
Date | Sample Location | pH | Alk | PO4 | Other | yes/no
For OHA use only:
Minimum Water Quality
Parameters as set by:
[7 empty] | pH | 7.2
[7 empty] | Alk | 16
PO4
Other
Total number of excursions during this monitoring period =
Send to dwp.dmce@state.or.us within 10 days after end of sampling period (October 10)
[5 empty] | Print Name: |  | Bob Zeller
Signature:
Date:
< Has sample
met the minimums?