|  |  |  |  |
| --- | --- | --- | --- |
| System Name | Brookings | PWS ID# | 4 1 00149 |
| Month/Year  | March 2025 | Entry Point: | A | Required Minimum Residual : | Variable – see column headers |
| Date | Time | Source(s) in use | Lowest free chlorine residual at WTP influent (minimum 0.1 mg/L) | In emergency, when influent not met – use filter trains & monitor at Entry Pt(minimum 0.3 mg/L) | Notes |
| 1 | 1350 | SRC-AA | 0.33 |  |  |
| 2 | 2140 | SRC-AA | 0.48 |  |  |
| 3 | 1230 | SRC-AA | 0.44 |  |  |
| 4 | 0120 | SRC-AA | 0.46 |  |  |
| 5 | 1825 | SRC-AA | 0.44 |  |  |
| 6 | 0340 | SRC-AA | 0.45 |  |  |
| 7 | 0325 | SRC-AA | 0.46 |  |  |
| 8 | 1920 | SRC-AA | 0.46 |  |  |
| 9 | 2025 | SRC-AA | 0.47 |  |  |
| 10 | 0115 | SRC-AA | 0.46 |  |  |
| 11 | 0832 | SRC-AA | 0.24 |  |  |
| 12 | 0130 | SRC-AA | 0.21 |  |  |
| 13 | 0635 | SRC-AA | 0.32 |  |  |
| 14 | 0800 | SRC-AA | 0.33 |  |  |
| 15 | 0840 | SRC-AA | 0.19 |  |  |
| 16 | 2300 | SRC-AA | 0.47 |  |  |
| 17 | 1120 | SRC-AA | 0.37 |  |  |
| 18 | 1145 | SRC-AA | 0.38 |  |  |
| 19 | 1200 | SRC-AA | 0.43 |  |  |
| 20 | 1949 | SRC-AA | 0.64 |  |  |
| 21 | 1225 | SRC-AA | 0.65 |  |  |
| 22 | 0455 | SRC-AA | 0.59 |  |  |
| 23 | 0245 | SRC-AA | 0.64 |  |  |
| 24 | 1757 | SRC-AA | 0.57 |  |  |
| 25 | 0902 | SRC-AA | 0.56 |  |  |
| 26 | 1220 | SRC-AA | 0.58 |  |  |
| 27 | 2115 | SRC-AA | 0.57 |  |  |
| 28 | 0505 | SRC-AA | 0.73 |  |  |
| 29 | 0350 | SRC-AA | 0.67 |  |  |
| 30 | 1040 | SRC-AA | 0.64 |  |  |
| 31 | 1845 | SRC-AA | 0.44 |  |  |
| Was the chlorine residual ever less than the required minimum residual of 0.1 mg/L? [ ] Yes [x] NoIf yes, what was the longest time period until the required level was restored?  |
| **GWS Serving 3,300 or Fewer** | **GWS Serving More Than 3,300** |
| If yes, did you monitor every four hours until the residual returned to       mg/L as required? [ ] Yes [ ] No *Attach those results and submit them with this form.* | Did continuous monitoring equipment fail at any time this reporting month? [ ]  Yes [x] NoIf yes, were grab samples collected every four hours until the continuous monitoring equipment was returned to service as required? [ ] Yes [ ]  No required since it was less than 4 hours.  | Date continuous monitoring equipment failed:      /       /      Date it was returned to service:       /       /       |
| Printed Name: Brenda L Vasquez | Title: DRC  | Operator Certification #: T2/D1070226 |
| Signature: Brenda L Vasquez  | Phone #: (541) 254-1909 | OR |
| Date: 04 / 07 / 2025 |  | Small Groundwater System [ ]  |

***Return by 10th of following month by either email*** ***dwp.dmce@odhsoha.oregon.******gov; fax 971-673-0694;***
***or mail to Drinking Water Services, PO Box 14350, Portland, OR 97293-0350.***

***August 22, 2019***