## Sheet1
State of Oregon Drinking Water Program
Monthly Disinfection Report for Ground Water Systems
System Name |  | City of Dayton |  | PWS # 4100252
Month/Year | 2023-06-01 |  | Entry Point WTP - A1 | Required Minimum Residual 0.6 mg/L
Date | Time | Source in Use | Lowest free chlorine residual at entry point to distribution system | Notes
1 | 8:23 | WTP - A1 | 0.79
2 | 8:37 |  | 0.8
3 | 6:50 |  | 0.78
4 | 7:25 |  | 0.78
5 | 7:29 |  | 0.8
6 | 9:52 |  | 0.78
7 | 7:20 |  | 0.77
8 | 8:48 |  | 0.81
9 | 8:54 |  | 0.8
10 | 6:30 |  | 0.83
11 | 6:29 |  | 0.8
12 | 10:13 |  | 1.24
13 | 6:56 |  | 0.81
14 | 7:09 |  | 0.82
15 | 7:52 |  | 0.82
16 | 8:05 |  | 0.8
17 | 7:42 |  | 0.82
18 | 7:15 |  | 0.82
19 | 7:01 |  | 0.82
20 | 7:20 |  | 0.82
21 | 6:57 |  | 0.82
22 | 7:14 |  | 0.82
23 | 6:30 |  | 0.83
24 | 7:54 |  | 0.77
25 | 8:04 |  | 0.78
26 | 8:11 |  | 82
27 | 9:05 |  | 0.82
28 | 6:42 |  | 0.81
29 | 8:15 |  | 0.82
30 | 8:57 |  | 0.82
WTP - A1
Was the chlorine residual ever less than the required minimum residual of 0.6 mg/L NO
If yes, what was the longest time period until the required level was restored ____ hours - if > 4 hours,
Drinking Water Program to be notified by end of next buisness day
GWS Servin 3,300 or Fewer
If yes, did you monitor every 4 hours
until the residual returned to 0.6 mg/L
as required YES NO
Attach those results and submit them
with this form
Printed Name Stephen Sagmiller TitlePublic Works Director Operator Certification # 6845
Signature _________________________________ Phone # 503-864-2221 | Stephen Sagmiller
Date ________________________ | 2023-07-04