State of Oregon Drinking Water Program

Monthly Disinfection Report for Ground Water Systems

| System Name |  | City of Dayton |  | PWS # 4100252 |
| --- | --- | --- | --- | --- |
| Month/Year | Oct.-25 |  | Entry Point WTP - A1 | Required Minimum Residual 0.6 mg/L |

| Date | Time | Source in Use | Lowest free chlorine residual at entry point to distribution system | Notes |
| --- | --- | --- | --- | --- |
| 1 | 0.82 | WTP - A1 | 8:00 |  |
| 2 | 0.80 |  | 7:51 |  |
| 3 | 0.87 |  | 7:55 |  |
| 4 | 0.85 |  | 7:56 |  |
| 5 | 0.84 |  | 8:02 |  |
| 6 | 0.84 |  | 7:47 |  |
| 7 | 0.84 |  | 7:21 |  |
| 8 | 0.82 |  | 7:44 |  |
| 9 | 0.84 |  | 8:07 |  |
| 10 | 0.84 |  | 8:01 |  |
| 11 | 0.81 |  | 8:30 |  |
| 12 | 0.84 |  | 8:02 |  |
| 13 | 0.81 |  | 8:08 |  |
| 14 | 0.81 |  | 7:41 |  |
| 15 | 0.83 |  | 7:51 |  |
| 16 | 0.81 |  | 8:02 |  |
| 17 | 0.83 |  | 7:00 |  |
| 18 | 0.86 |  | 7:29 |  |
| 19 | 0.81 |  | 7:28 |  |
| 20 | 0.84 |  | 7:55 |  |
| 21 | 0.80 |  | 7:50 |  |
| 22 | 0.83 |  | 7:51 |  |
| 23 | 0.83 |  | 8:09 |  |
| 24 | 0.84 |  | 7:52 |  |
| 25 | 0.81 |  | 8:10 |  |
| 26 | 0.83 |  | 8:23 |  |
| 27 | 0.84 |  | 7:55 |  |
| 28 | 0.83 |  | 8:03 |  |
| 29 | 0.82 |  | 7:53 |  |
| 30 | 0.84 | WTP - A1 | 7:49 |  |
| 31 | 0.80 |  | 7:51 |  |
| Was the chlorine residual ever less than the required minimum residual of 0.6 mg/L NO |  |  |  |  |
| If yes, what was the longest time period until the required level was restored hours - if > 4 hours, |  |  |  |  |
| Drinking Water Program to be notified by end of next buisness day |  |  |  |  |
| GWS Servin 3,300 or Fewer |  |  |  |  |
| If yes, did you monitor every 4 hours |  |  |  |  |
| until the residual returned to 0.6 mg/L |  |  |  |  |
| as required YES NO |  |  |  |  |
| Attach those results and submit them |  |  |  |  |
| with this form |  |  |  |  |
| Printed Name Don Cutler Title Public Works Supervisor Operator Certification # 149310 DRC – John Lindow Signature Don Cutler Date 11/3/2025 |  |  |  |  |