|  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| System Name | | | Idaho Power- Oxbow Village | | | | | | | PWS ID# | | 4 1 00384 | |
| Month/Year | | Sept/2022 | | | Entry Point: | EP-B, Entry Point for Copperfield Park Well | | | Required Minimum Residual | | | | 0.2 mg/L |
|  |  | | |  | | |  | | | |  | | |
| Date | Time | | | Source(s) in use | | | | Lowest free chlorine  residual at entry point to  distribution system (mg/L) | | | Notes | | |
| 1 | 0700 | | | Booster Pump | | | | .47 | | |  | | |
| 2 | 0700 | | | Booster Pump | | | | .52 | | |  | | |
| 3 | 0700 | | | Booster Pump | | | | .45 | | |  | | |
| 4 | 0700 | | | Booster Pump | | | | .45 | | |  | | |
| 5 | 0700 | | | Booster Pump | | | | .47 | | |  | | |
| 6 | 0700 | | | Booster Pump | | | | .41 | | | House 567 .30 | | |
| 7 | 0700 | | | Booster Pump | | | | .47 | | |  | | |
| 8 | 0700 | | | Booster Pump | | | | .40 | | | House 5613 .26 | | |
| 9 | 0700 | | | Booster Pump | | | | .44 | | |  | | |
| 10 | 0700 | | | Booster Pump | | | | .46 | | |  | | |
| 11 | 0700 | | | Booster Pump | | | | .47 | | |  | | |
| 12 | 0700 | | | Booster Pump | | | | .46 | | | House 851 .34 | | |
| 13 | 0700 | | | Booster Pump | | | | .50 | | |  | | |
| 14 | 0700 | | | Booster Pump | | | | .52 | | |  | | |
| 15 | 0700 | | | Booster Pump | | | | .45 | | | House 5620 .36 | | |
| 16 | 0700 | | | Booster Pump | | | | .48 | | |  | | |
| 17 | 0700 | | | Booster Pump | | | | .42 | | |  | | |
| 18 | 0700 | | | Booster Pump | | | | .41 | | |  | | |
| 19 | 0700 | | | Booster Pump | | | | .41 | | | House 567 .33 | | |
| 20 | 0700 | | | Booster Pump | | | | .43 | | |  | | |
| 21 | 0700 | | | Booster Pump | | | | .41 | | |  | | |
| 22 | 0700 | | | Booster Pump | | | | .44 | | | House 5613 .34 | | |
| 23 | 0700 | | | Booster Pump | | | | .43 | | |  | | |
| 24 | 0700 | | | Booster Pump | | | | .40 | | |  | | |
| 25 | 0700 | | | Booster Pump | | | | .47 | | |  | | |
| 26 | 0700 | | | Booster Pump | | | | .38 | | | House 851.30 | | |
| 27 | 0700 | | | Booster Pump | | | | .41 | | |  | | |
| 28 | 0700 | | | Booster Pump | | | | .46 | | |  | | |
| 29 | 0700 | | | Booster Pump | | | | .43 | | | House 5620 .33 | | |
| 30 | 0700 | | | Booster Pump | | | | .38 | | |  | | |
| 31 |  | | | Booster Pump | | | |  | | |  | | |

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| Was the chlorine residual ever less than the required minimum residual of 0.2 mg/L?  Yes  No  If yes, what was the longest time period until the required level was restored?       hours | | | | |
| **GWS Serving 3,300 or Fewer** | **GWS Serving More Than 3,300** | | | |
| If yes, did you monitor every four hours until the residual returned to 0.2 mg/L? 🞏Yes 🞏 No  *Attach those results and submit them with this form.* | Did continuous monitoring equipment fail at any time this reporting month?  Yes  No  If yes, were grab samples collected every four hours until the continuous monitoring equipment was returned to service?  Yes  No  *Attach grab sample results and submit them with this form.* | | | Date continuous monitoring equipment failed:        /       /  Date it was returned to service:          /       / |
| Printed Name: Heath Phelps | | Title: Building Maintenance Tec | Operator Certification #: | |
| Signature: | | Phone #: ( 541) 785-7225 | OR | |
| Date: 09 / 30 / 2022 | |  | Small Groundwater System | |