|  |  |  |  |
| --- | --- | --- | --- |
| System Name | Idaho Power- Oxbow Village | PWS ID# | 4 1 00384 |
| Month/Year |  Sept/2022  | Entry Point: | EP-B, Entry Point for Copperfield Park Well | Required Minimum Residual  | 0.2 mg/L  |
|  |  |  |  |  |
| Date | Time | Source(s) in use | Lowest free chlorine residual at entry point to distribution system (mg/L) | Notes |
| 1 | 0700 | Booster Pump | .47 |       |
| 2 | 0700 | Booster Pump | .52 |       |
| 3 | 0700 | Booster Pump | .45 |       |
| 4 | 0700 | Booster Pump | .45 |       |
| 5 | 0700 | Booster Pump | .47 |       |
| 6 | 0700 | Booster Pump | .41 | House 567 .30 |
| 7 | 0700 | Booster Pump | .47 |       |
| 8 | 0700 | Booster Pump | .40 | House 5613 .26  |
| 9 | 0700 | Booster Pump | .44 |       |
| 10 | 0700 | Booster Pump | .46 |       |
| 11 | 0700 | Booster Pump | .47 |       |
| 12 | 0700 | Booster Pump | .46 | House 851 .34 |
| 13 | 0700 | Booster Pump | .50 |       |
| 14 | 0700 | Booster Pump | .52 |       |
| 15 | 0700 | Booster Pump | .45 | House 5620 .36  |
| 16 | 0700 | Booster Pump | .48 |       |
| 17 | 0700 | Booster Pump | .42 |       |
| 18 | 0700 | Booster Pump | .41 |       |
| 19 | 0700 | Booster Pump | .41 | House 567 .33 |
| 20 | 0700 | Booster Pump | .43 |       |
| 21 | 0700 | Booster Pump | .41 |       |
| 22 | 0700 | Booster Pump | .44 | House 5613 .34  |
| 23 | 0700 | Booster Pump | .43 |       |
| 24 | 0700 | Booster Pump | .40 |       |
| 25 | 0700 | Booster Pump | .47 |       |
| 26 | 0700 | Booster Pump | .38 | House 851.30  |
| 27 | 0700 | Booster Pump | .41 |       |
| 28 | 0700 | Booster Pump | .46 |       |
| 29 | 0700 | Booster Pump | .43 | House 5620 .33 |
| 30 | 0700 | Booster Pump | .38 |       |
| 31 |       | Booster Pump |       |       |

|  |
| --- |
| Was the chlorine residual ever less than the required minimum residual of 0.2 mg/L? [ ]  Yes [x]  NoIf yes, what was the longest time period until the required level was restored?       hours |
| **GWS Serving 3,300 or Fewer** | **GWS Serving More Than 3,300** |
| If yes, did you monitor every four hours until the residual returned to 0.2 mg/L? 🞏Yes 🞏 No *Attach those results and submit them with this form.* | Did continuous monitoring equipment fail at any time this reporting month? [ ]  Yes [ ]  NoIf yes, were grab samples collected every four hours until the continuous monitoring equipment was returned to service? [ ]  Yes [ ]  No *Attach grab sample results and submit them with this form.* | Date continuous monitoring equipment failed:      /       /      Date it was returned to service:       /       /       |
| Printed Name: Heath Phelps | Title: Building Maintenance Tec  | Operator Certification #:       |
| Signature:  | Phone #: ( 541) 785-7225 | OR |
| Date: 09 / 30 / 2022 |  | Small Groundwater System [ ]  |