## 2024
State of Oregon Drinking Water Program
Monthly Disinfection Report for Ground Water Systems
System Name: |  | Siuslaw Marina |  | PWS ID# 41 - 05289
Month/Year: |  | 2025-08-01 |  | Required Minimum Residual: 0.40 mg/L
Date | Time | Source(s) in Use | Lowest free chlorine residual at entry point to distribution system (mg/L) | Notes
1 | 14:00 | WELL (LANE19133) | 0.41
2 | 14:00 | WELL (LANE19133) | 0.44
3 | 10:00 | WELL (LANE19133) | 0.46
4 | 10:00 | WELL (LANE19133) | 0.42
5 | 6:00 | WELL (LANE19133) | 0.4
6 | 14:00 | WELL (LANE19133) | 0.43
7 | 10:00 | WELL (LANE19133) | 0.42
8 | 6:00 | WELL (LANE19133) | 0.4
9 | 18:00 | WELL (LANE19133) | 0.52
10 | 18:00 | WELL (LANE19133) | 0.56
11 | 18:00 | WELL (LANE19133) | 0.51
12 | 18:00 | WELL (LANE19133) | 0.42
13 | 10:00 | WELL (LANE19133) | 0.43
14 | 10:00 | WELL (LANE19133) | 0.5
15 | 6:00 | WELL (LANE19133) | 0.57
16 | 14:00 | WELL (LANE19133) | 0.51
17 | 14:00 | WELL (LANE19133) | 0.82
18 | 6:00 | WELL (LANE19133) | 0.4
19 | 6:00 | WELL (LANE19133) | 0.48
20 | 18:00 | WELL (LANE19133) | 0.46
21 | 10:00 | WELL (LANE19133) | 0.43
22 | 10:00 | WELL (LANE19133) | 0.48
23 | 14:00 | WELL (LANE19133) | 0.5
24 | 6:00 | WELL (LANE19133) | 0.86
25 | 6:00 | WELL (LANE19133) | 0.49
26 | 6:00 | WELL (LANE19133) | 0.45
27 | 10:00 | WELL (LANE19133) | 0.46
28 | 14:00 | WELL (LANE19133) | 0.44
29 | 14:00 | WELL (LANE19133) | 0.46
30 | 18:00 | WELL (LANE19133) | 0.49
31 | 19:00 | WELL (LANE19133) | 0.41
Was the chlorine residual ever less than the required minimum residual of .40 mg/L ____ Yes __X__ No
If yes, what was the longest time period until the required level was restored? _____ hours
GWS Serving 3,300 or Fewer |  |  | GWS Serving More Than 3,300
If yes, did you monitor every four hours until the residual returned to .40 mg/L? |  |  | Did continuous monitoring equipment fail at any time this reporting month? ___Yes ___No |  | Date continuous monitoring equipment failed: / /
Attach those results and submit them with this form. |  |  | If yes, were grab samples collected every four hours until the continuous monitoring equipment was returned to service? ___Yes ___No |  | Date it was returned to service:
|  |  | Attach grab sample results and submit them with this form. |  | / /
Printed Name: |  | Dan Reitz | Title: Vice- President | Operator Certification #:
|  |  | Oregon Water Services, Inc. |  |  | 6528
Signature: |  |  | Phone#: (541) 342-1718 | OR
Small Ground Water System
Date: | 2025-09-08