## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-01-01
System Name: | Barclay Meadows Water Co-Op |  |  | ID#: 39 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0
2 |  |  |  | 0
3 |  |  |  | 0
4 |  |  |  | 0
5 |  |  |  | 0
6 |  |  |  | 0
7 |  |  |  | 0
8 |  |  |  | 0
9 |  |  |  | 0
10 |  |  |  | 0
11 |  |  |  | 0
12 |  |  |  | 0
13 |  |  |  | 0
14 |  |  |  | 0
15 |  |  |  | 0
16 |  |  |  | 0
17 |  |  |  | 0
18 |  |  |  | 0
19 |  |  |  | 0
20 |  |  |  | 0
21 |  |  |  | 0
22 |  |  |  | 0
23 |  |  |  | 0
24 |  |  |  | 0
25 |  |  |  | 0
26 |  |  |  | 0
27 |  |  |  | 0
28 |  |  |  | 0
29 |  |  |  | 0
30 |  |  |  | 0
31 |  |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Robert Riecke
[5 empty] | SIGNATURE: |  |  | DATE: January 2021
[5 empty] | PHONE #: ( 541 ) 528-3257 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Barclay Meadows Water Co-Op |  | ID#: 39 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.5 | 1440 | 2160 | 11.1 | 7.4 | 43.6676 | YES | 3203
2 | 1.1 | 1440 | 1584 | 11.5 | 7.8 | 46.798 | YES | 3274
3 | 0.8 | 1440 | 1152 | 11.1 | 7.8 | 46.4462 | YES | 2716
4 | 0.8 | 1440 | 1152 | 11.2 | 7.9 | 47.8013 | YES | 2410
5 | 0.8 | 1440 | 1152 | 10.6 | 8.1 | 53.4341 | YES | 1767
6 | 0.8 | 1440 | 1152 | 12.1 | 8 | 46.6493 | YES | 2005
7 | 0.8 | 1440 | 1152 | 11.2 | 8.1 | 51.3259 | YES | 1781
8 | 0.8 | 1440 | 1152 | 10.8 | 8.3 | 56.6437 | YES | 1898
9 | 0.9 | 1440 | 1296 | 11 | 8.4 | 58.6081 | YES | 1927
10 | 1 | 1440 | 1440 | 10.4 | 8.7 | 68.8768 | YES | 2646
11 | 1 | 1440 | 1440 | 11.1 | 8.5 | 61.0595 | YES | 1383
12 | 0.8 | 1440 | 1152 | 11.3 | 8.6 | 61.0197 | YES | 1857
13 | 1 | 1440 | 1440 | 11.3 | 8.7 | 64.7665 | YES | 8570
14 | 1 | 1440 | 1440 | 10.6 | 8.4 | 60.9233 | YES | 3902
15 | 1.1 | 1440 | 1584 | 11.6 | 8.5 | 59.712 | YES | 2851
16 | 1.1 | 1440 | 1584 | 11.2 | 8.4 | 59.1765 | YES | 1719
17 | 1.2 | 1440 | 1728 | 10.7 | 8.7 | 69.0775 | YES | 2784
18 | 1.2 | 1440 | 1728 | 10.1 | 8.6 | 69.396 | YES | 3310
19 | 1.33 | 1440 | 1915.2 | 11.3 | 8.5 | 62.5942 | YES | 2464
20 | 1.28 | 1440 | 1843.2 | 9.6 | 8.6 | 72.4974 | YES | 1909
21 | 1.06 | 1440 | 1526.4 | 9.6 | 8.6 | 70.6458 | YES | 2328
22 | 1.42 | 1440 | 2044.8 | 9.6 | 8.6 | 73.7024 | YES | 2938
23 | 1.26 | 1440 | 1814.4 | 9.3 | 8.4 | 68.6252 | YES | 2797
24 | 1.43 | 1440 | 2059.2 | 8.9 | 8.6 | 77.4357 | YES | 2338
25 | 4.49 | 1440 | 6465.6 | 8.8 | 8.6 | 112.328 | YES | 1916
26 | 1.45 | 1440 | 2088 | 8.7 | 8.6 | 78.6982 | YES | 1409
27 | 1.38 | 1440 | 1987.2 | 8.7 | 8.6 | 78.0495 | YES | 1345
28 | 1.26 | 1440 | 1814.4 | 7.7 | 8.4 | 76.6024 | YES | 1580
29 | 1.24 | 1440 | 1785.6 | 7.4 | 8.6 | 83.9894 | YES | 1478
30 | 1.24 | 1440 | 1785.6 | 9 | 8.6 | 75.1979 | YES | 1254
31 | 1.28 | 1440 | 1843.2 | 9.5 | 7.6 | 50.8387 | YES | 2351
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2