## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-03-01
System Name: | Barclay Meadows Water Co-Op |  |  | ID#: 39 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0
2 |  |  |  | 0
3 |  |  |  | 0
4 |  |  |  | 0
5 |  |  |  | 0
6 |  |  |  | 0
7 |  |  |  | 0
8 |  |  |  | 0
9 |  |  |  | 0
10 |  |  |  | 0
11 |  |  |  | 0
12 |  |  |  | 0
13 |  |  |  | 0
14 |  |  |  | 0
15 |  |  |  | 0
16 |  |  |  | 0
17 |  |  |  | 0
18 |  |  |  | 0
19 |  |  |  | 0
20 |  |  |  | 0
21 |  |  |  | 0
22 |  |  |  | 0
23 |  |  |  | 0
24 |  |  |  | 0
25 |  |  |  | 0
26 |  |  |  | 0
27 |  |  |  | 0
28 |  |  |  | 0
29 |  |  |  | 0
30 |  |  |  | 0
31 |  |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Robert Riecke
[5 empty] | SIGNATURE: |  |  | DATE:31 March 2021
[5 empty] | PHONE #: ( 541 ) 528-3257 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Barclay Meadows Water Co-Op |  | ID#: 39 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.01 | 1440 | 1454.4 | 8.1 | 8.1 | 64.8544 | YES | 1108
2 | 1.12 | 1440 | 1612.8 | 7.2 | 8.3 | 75.1766 | YES | 1060
3 | 1.07 | 1440 | 1540.8 | 8.3 | 8.3 | 69.2951 | YES | 1130
4 | 1.07 | 1440 | 1540.8 | 8.3 | 8.3 | 69.2951 | YES | 762
5 | 1.1 | 1440 | 1584 | 8.6 | 8.3 | 68.1249 | YES | 1018
6 | 1.13 | 1440 | 1627.2 | 8.5 | 8.3 | 68.8348 | YES | 2050
7 | 1.2 | 1440 | 1728 | 7.9 | 8.5 | 77.8284 | YES | 1925
8 | 1.2 | 1440 | 1728 | 7.8 | 8.5 | 78.3676 | YES | 1245
9 | 1.22 | 1440 | 1756.8 | 7.6 | 8.5 | 79.6461 | YES | 1430
10 | 1.22 | 1440 | 1756.8 | 6.5 | 8.6 | 89.1924 | YES | 1158
11 | 1.08 | 1440 | 1555.2 | 7.3 | 8.5 | 79.9786 | YES | 1453
12 | 1.14 | 1440 | 1641.6 | 8.2 | 8.5 | 75.6963 | YES | 1213
13 | 1.1 | 1440 | 1584 | 7.4 | 8.2 | 71.3132 | YES | 1168
14 | 0.94 | 1440 | 1353.6 | 8.5 | 8.3 | 67.3187 | YES | 1358
15 | 0.79 | 1440 | 1137.6 | 7.7 | 8.3 | 69.8701 | YES | 1825
16 | 0.97 | 1440 | 1396.8 | 6.2 | 8.4 | 82.102 | YES | 1135
17 | 0.7 | 1440 | 1008 | 5.9 | 8.4 | 81.1848 | YES | 1612
18 | 1.17 | 1440 | 1684.8 | 7.9 | 8.2 | 69.4775 | YES | 2343
19 | 0.68 | 1440 | 979.2 | 8.3 | 8.2 | 63.8356 | YES | 1973
20 | 0.96 | 1440 | 1382.4 | 8.6 | 8.2 | 64.6214 | YES | 2522
21 | 0.85 | 1440 | 1224 | 8.1 | 8.2 | 66.0109 | YES | 1860
22 | 0.99 | 1440 | 1425.6 | 8.9 | 8.3 | 65.8875 | YES | 2040
23 | 0.66 | 1440 | 950.4 | 7.8 | 8.3 | 68.3425 | YES | 2200
24 | 1.02 | 1440 | 1468.8 | 8.3 | 8.2 | 66.4231 | YES | 1885
25 | 1.15 | 1440 | 1656 | 8.4 | 8.2 | 66.9821 | YES | 1350
26 | 1.24 | 1440 | 1785.6 | 8 | 8.2 | 69.5721 | YES | 1995
27 | 1.34 | 1440 | 1929.6 | 7.9 | 8.1 | 68.3361 | YES | 2430
28 | 1.84 | 1440 | 2649.6 | 8 | 8.2 | 74.6606 | YES | 3645
29 | 1.52 | 1440 | 2188.8 | 7.5 | 8.2 | 74.4146 | YES | 1260
30 | 1.14 | 1440 | 1641.6 | 6.8 | 8.2 | 74.6677 | YES | 1965
31 | 1.28 | 1440 | 1843.2 | 7 | 8.2 | 74.8722 | YES | 1725
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2