## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-08-01
System Name: | Barclay Meadows Water Co-Op |  |  | ID#: 39 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0
2 |  |  |  | 0
3 |  |  |  | 0
4 |  |  |  | 0
5 |  |  |  | 0
6 |  |  |  | 0
7 |  |  |  | 0
8 |  |  |  | 0
9 |  |  |  | 0
10 |  |  |  | 0
11 |  |  |  | 0
12 |  |  |  | 0
13 |  |  |  | 0
14 |  |  |  | 0
15 |  |  |  | 0
16 |  |  |  | 0
17 |  |  |  | 0
18 |  |  |  | 0
19 |  |  |  | 0
20 |  |  |  | 0
21 |  |  |  | 0
22 |  |  |  | 0
23 |  |  |  | 0
24 |  |  |  | 0
25 |  |  |  | 0
26 |  |  |  | 0
27 |  |  |  | 0
28 |  |  |  | 0
29 |  |  |  | 0
30 |  |  |  | 0
31 |  |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Robert Riecke
[5 empty] | SIGNATURE: |  |  | 2021-08-31
[5 empty] | PHONE #: ( 541 ) 528-3257 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Barclay Meadows Water Co-Op |  | ID#: 39 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.99 | 1440 | 1425.6 | 14.8 | 7.8 | 37.0785 | YES | 4290
2 | 1 | 1440 | 1440 | 14.3 | 7.8 | 38.3738 | YES | 5900
3 | 0.98 | 1440 | 1411.2 | 14.1 | 7.8 | 38.7986 | YES | 4970
4 | 0.96 | 1440 | 1382.4 | 13.6 | 7.8 | 40.0165 | YES | 6710
5 | 0.97 | 1440 | 1396.8 | 14.6 | 7.8 | 37.4892 | YES | 4500
6 | 0.95 | 1440 | 1368 | 15.4 | 7.8 | 35.4676 | YES | 4230
7 | 0.88 | 1440 | 1267.2 | 16.2 | 7.8 | 33.3625 | YES | 4280
8 | 0.93 | 1440 | 1339.2 | 14.8 | 7.8 | 36.827 | YES | 5380
9 | 0.89 | 1440 | 1281.6 | 13.3 | 7.8 | 40.4982 | YES | 7810
10 | 0.95 | 1440 | 1368 | 13.5 | 7.8 | 40.2371 | YES | 10080
11 | 0.92 | 1440 | 1324.8 | 15.2 | 7.8 | 35.8202 | YES | 3530
12 | 0.93 | 1440 | 1339.2 | 14.4 | 7.8 | 37.8186 | YES | 2790
13 | 0.92 | 1440 | 1324.8 | 14.6 | 7.8 | 37.2772 | YES | 9960
14 | 1.1 | 1440 | 1584 | 15.8 | 7.8 | 35.13 | YES | 3160
15 | 1.03 | 1440 | 1483.2 | 14.4 | 7.9 | 39.6858 | YES | 4725
16 | 1.04 | 1440 | 1497.6 | 14.9 | 7.8 | 37.0425 | YES | 2785
17 | 0.83 | 1440 | 1195.2 | 14.8 | 7.8 | 36.4115 | YES | 1770
18 | 0.9 | 1440 | 1296 | 14.4 | 7.8 | 37.6901 | YES | 1270
19 | 1.13 | 1440 | 1627.2 | 15.2 | 7.8 | 36.6842 | YES | 1140
20 | 1.04 | 1440 | 1497.6 | 15 | 7.8 | 36.7973 | YES | 2340
21 | 1 | 1440 | 1440 | 14.8 | 7.8 | 37.1206 | YES | 1550
22 | 1.04 | 1440 | 1497.6 | 14.5 | 7.8 | 38.0398 | YES | 3435
23 | 0.86 | 1440 | 1238.4 | 13.1 | 7.8 | 40.8997 | YES | 2765
24 | 0.86 | 1440 | 1238.4 | 13.2 | 7.8 | 40.6294 | YES | 2010
25 | 0.98 | 1440 | 1411.2 | 14.4 | 7.7 | 36.6561 | YES | 2720
26 | 1.02 | 1440 | 1468.8 | 14.7 | 7.7 | 36.096 | YES | 1630
27 | 0.92 | 1440 | 1324.8 | 14.4 | 7.8 | 37.7757 | YES | 1620
28 | 0.87 | 1440 | 1252.8 | 13.9 | 7.8 | 38.8299 | YES | 2580
29 | 0.61 | 1440 | 878.4 | 13.8 | 7.8 | 37.9532 | YES | 3320
30 | 0.85 | 1440 | 1224 | 13.3 | 7.8 | 40.3152 | YES | 2600
31 | 1.13 | 1440 | 1627.2 | 13 | 7.8 | 42.4492 | YES | 3030
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2