## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-12-01
System Name: | Barclay Meadows Water Co-Op |  |  | ID#: 39 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0
2 |  |  |  | 0
3 |  |  |  | 0
4 |  |  |  | 0
5 |  |  |  | 0
6 |  |  |  | 0
7 |  |  |  | 0
8 |  |  |  | 0
9 |  |  |  | 0
10 |  |  |  | 0
11 |  |  |  | 0
12 |  |  |  | 0
13 |  |  |  | 0
14 |  |  |  | 0
15 |  |  |  | 0
16 |  |  |  | 0
17 |  |  |  | 0
18 |  |  |  | 0
19 |  |  |  | 0
20 |  |  |  | 0
21 |  |  |  | 0
22 |  |  |  | 0
23 |  |  |  | 0
24 |  |  |  | 0
25 |  |  |  | 0
26 |  |  |  | 0
27 |  |  |  | 0
28 |  |  |  | 0
29 |  |  |  | 0
30 |  |  |  | 0
31 |  |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Robert Riecke
[5 empty] | SIGNATURE: |  |  | DATE:Dec 2021
[5 empty] | PHONE #: ( 541 ) 528-3257 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Barclay Meadows Water Co-Op |  | ID#: 39 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.85 | 1440 | 1224 | 9.3 | 7.8 | 52.6751 | YES | 955
2 | 0.93 | 1440 | 1339.2 | 9.3 | 7.8 | 53.1619 | YES | 1185
3 | 0.81 | 1440 | 1166.4 | 9.2 | 7.8 | 52.7866 | YES | 1375
4 | 0.94 | 1440 | 1353.6 | 9 | 7.7 | 52.3973 | YES | 1190
5 | 0.46 | 1440 | 662.4 | 8.1 | 7.7 | 52.6726 | YES | 1115
6 | 1.93 | 1440 | 2779.2 | 8.6 | 7.5 | 56.156 | YES | 1010
7 | 1.66 | 1440 | 2390.4 | 9.1 | 7.5 | 52.6339 | YES | 455
8 | 1.39 | 1440 | 2001.6 | 9.2 | 7.6 | 52.53 | YES | 810
9 | 1.25 | 1440 | 1800 | 8.9 | 7.7 | 54.6669 | YES | 735
10 | 1.19 | 1440 | 1713.6 | 7.5 | 7.7 | 59.676 | YES | 550
11 | 1.08 | 1440 | 1555.2 | 9.1 | 7.7 | 52.8911 | YES | 1140
12 | 0.59 | 1440 | 849.6 | 7.6 | 7.6 | 53.3481 | YES | 1000
13 | 0.59 | 1440 | 849.6 | 6.2 | 7.7 | 60.7902 | YES | 850
14 | 0.79 | 1440 | 1137.6 | 5.9 | 7.7 | 63.5057 | YES | 790
15 | 0.78 | 1440 | 1123.2 | 6.2 | 7.8 | 64.4466 | YES | 600
16 | 0.73 | 1440 | 1051.2 | 5.8 | 7.7 | 63.4939 | YES | 680
17 | 0.68 | 1440 | 979.2 | 7.6 | 7.7 | 55.8738 | YES | 870
18 | 0.6 | 1440 | 864 | 8.4 | 7.7 | 52.46 | YES | 540
19 | 1.59 | 1440 | 2289.6 | 8.3 | 7.6 | 57.1148 | YES | 1760
20 | 1.38 | 1440 | 1987.2 | 8.4 | 7.6 | 55.3702 | YES | 675
21 | 0.99 | 1440 | 1425.6 | 8.6 | 7.6 | 52.2315 | YES | 415
22 | 0.8 | 1440 | 1152 | 9.2 | 7.7 | 50.876 | YES | 1200
23 | 0.72 | 1440 | 1036.8 | 8.5 | 7.5 | 49.1954 | YES | 1020
24 | 0.48 | 1440 | 691.2 | 7.7 | 7.6 | 52.3252 | YES | 630
25 | 0.96 | 1440 | 1382.4 | 6.6 | 7.6 | 59.568 | YES | 720
26 | 1.36 | 1440 | 1958.4 | 5.1 | 7.6 | 69.1359 | YES | 440
27 | 0.98 | 1440 | 1411.2 | 4.7 | 7.5 | 65.5279 | YES | 875
28 | 0.84 | 1440 | 1209.6 | 4.4 | 7.6 | 68.24 | YES | 785
29 | 0.66 | 1440 | 950.4 | 4.7 | 7.5 | 63.1247 | YES | 890
30 | 0.9 | 1440 | 1296 | 4.9 | 7.6 | 66.4106 | YES | 760
31 | 1.24 | 1440 | 1785.6 | 4.9 | 7.4 | 64.2542 | YES | 805
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2