## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-01-01
System Name: | Barclay Meadows Water Co-Op |  |  | ID#: 39 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0
2 |  |  |  | 0
3 |  |  |  | 0
4 |  |  |  | 0
5 |  |  |  | 0
6 |  |  |  | 0
7 |  |  |  | 0
8 |  |  |  | 0
9 |  |  |  | 0
10 |  |  |  | 0
11 |  |  |  | 0
12 |  |  |  | 0
13 |  |  |  | 0
14 |  |  |  | 0
15 |  |  |  | 0
16 |  |  |  | 0
17 |  |  |  | 0
18 |  |  |  | 0
19 |  |  |  | 0
20 |  |  |  | 0
21 |  |  |  | 0
22 |  |  |  | 0
23 |  |  |  | 0
24 |  |  |  | 0
25 |  |  |  | 0
26 |  |  |  | 0
27 |  |  |  | 0
28 |  |  |  | 0
29 |  |  |  | 0
30 |  |  |  | 0
31 |  |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Robert Riecke
[5 empty] | SIGNATURE: |  |  | 2022-01-31
[5 empty] | PHONE #: ( 541 ) 528-3257 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Barclay Meadows Water Co-Op |  | ID#: 39 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.82 | 1440 | 1180.8 | 4.8 | 7.8 | 71.2596 | YES | 1895
2 | 0.78 | 1440 | 1123.2 | 5.3 | 7.5 | 61.4529 | YES | 1208
3 | 0.91 | 1440 | 1310.4 | 7.2 | 7.5 | 54.8589 | YES | 1502
4 | 0.97 | 1440 | 1396.8 | 6.3 | 7.3 | 54.6266 | YES | 725
5 | 0.92 | 1440 | 1324.8 | 7.3 | 7.3 | 50.7875 | YES | 730
6 | 0.9 | 1440 | 1296 | 9.3 | 7.3 | 44.3636 | YES | 855
7 | 0.96 | 1440 | 1382.4 | 8.4 | 7.2 | 45.7638 | YES | 935
8 | 0.9 | 1440 | 1296 | 8 | 7.2 | 46.6748 | YES | 1445
9 | 1.07 | 1440 | 1540.8 | 7.7 | 7.1 | 46.8555 | YES | 1635
10 | 1.02 | 1440 | 1468.8 | 8 | 7.2 | 47.3161 | YES | 1950
11 | 0.92 | 1440 | 1324.8 | 9.7 | 7.3 | 43.3065 | YES | 2025
12 | 0.92 | 1440 | 1324.8 | 9.4 | 7.2 | 42.6479 | YES | 940
13 | 1.09 | 1440 | 1569.6 | 9.9 | 7.3 | 43.5671 | YES | 700
14 | 1.15 | 1440 | 1656 | 9.2 | 7.3 | 45.9407 | YES | 740
15 | 1.06 | 1440 | 1526.4 | 8.8 | 7.4 | 48.3802 | YES | 1380
16 | 0.96 | 1440 | 1382.4 | 8.4 | 7.4 | 49.1235 | YES | 1285
17 | 1.13 | 1440 | 1627.2 | 8.3 | 7.3 | 48.6614 | YES | 875
18 | 1.14 | 1440 | 1641.6 | 8.9 | 7.3 | 46.8108 | YES | 1105
19 | 1.1 | 1440 | 1584 | 9.2 | 7.3 | 45.6809 | YES | 786
20 | 1.08 | 1440 | 1555.2 | 9.9 | 7.3 | 43.518 | YES | 599
21 | 1.03 | 1440 | 1483.2 | 8.6 | 7.4 | 48.8617 | YES | 785
22 | 1.04 | 1440 | 1497.6 | 7.4 | 7.4 | 53.008 | YES | 1225
23 | 1 | 1440 | 1440 | 7.2 | 7.3 | 51.5998 | YES | 1175
24 | 0.99 | 1440 | 1425.6 | 7.2 | 7.4 | 53.4169 | YES | 1145
25 | 1.32 | 1440 | 1900.8 | 6.9 | 7.4 | 56.6227 | YES | 960
26 | 0.98 | 1440 | 1411.2 | 6.6 | 7.4 | 55.5546 | YES | 890
27 | 0.93 | 1440 | 1339.2 | 6.5 | 7.3 | 53.6486 | YES | 1185
28 | 1.02 | 1440 | 1468.8 | 5.9 | 7.2 | 54.4531 | YES | 1040
29 | 1.13 | 1440 | 1627.2 | 6.1 | 6.3 | 39.5904 | YES | 1585
30 | 1.11 | 1440 | 1598.4 | 7.2 | 7 | 46.9665 | YES | 1675
31 | 1.03 | 1440 | 1483.2 | 7.5 | 7.3 | 50.7479 | YES | 1140
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2