## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2002-05-01
System Name: | Barclay Meadows Water Co-Op |  |  | ID#: 39 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0
2 |  |  |  | 0
3 |  |  |  | 0
4 |  |  |  | 0
5 |  |  |  | 0
6 |  |  |  | 0
7 |  |  |  | 0
8 |  |  |  | 0
9 |  |  |  | 0
10 |  |  |  | 0
11 |  |  |  | 0
12 |  |  |  | 0
13 |  |  |  | 0
14 |  |  |  | 0
15 |  |  |  | 0
16 |  |  |  | 0
17 |  |  |  | 0
18 |  |  |  | 0
19 |  |  |  | 0
20 |  |  |  | 0
21 |  |  |  | 0
22 |  |  |  | 0
23 |  |  |  | 0
24 |  |  |  | 0
25 |  |  |  | 0
26 |  |  |  | 0
27 |  |  |  | 0
28 |  |  |  | 0
29 |  |  |  | 0
30 |  |  |  | 0
31 |  |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Robert Riecke
[5 empty] | SIGNATURE: |  |  | DATE:05/2022
[5 empty] | PHONE #: ( 541 ) 528-3257 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Barclay Meadows Water Co-Op |  | ID#: 39 |  | Month/Year: | 2022-05-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.65 | 1440 | 936 | 10.9 | 7.8 | 46.2714 | YES | 985
2 | 0.72 | 1440 | 1036.8 | 10.2 | 7.8 | 48.8639 | YES | 872
3 | 0.69 | 1440 | 993.6 | 9.6 | 7.8 | 50.6875 | YES | 1088
4 | 0.64 | 1440 | 921.6 | 9.6 | 7.9 | 52.2291 | YES | 905
5 | 0.68 | 1440 | 979.2 | 9.6 | 7.8 | 50.6295 | YES | 1078
6 | 0.72 | 1440 | 1036.8 | 9.8 | 7.8 | 50.1862 | YES | 963
7 | 0.63 | 1440 | 907.2 | 9.2 | 7.8 | 51.7064 | YES | 1439
8 | 0.56 | 1440 | 806.4 | 9.6 | 7.8 | 49.9388 | YES | 1690
9 | 0.58 | 1440 | 835.2 | 9.6 | 7.8 | 50.0532 | YES | 980
10 | 0.65 | 1440 | 936 | 9.3 | 7.8 | 51.4791 | YES | 740
11 | 0.6 | 1440 | 864 | 9.6 | 7.8 | 50.1679 | YES | 1295
12 | 0.68 | 1440 | 979.2 | 9.7 | 7.8 | 50.292 | YES | 1110
13 | 0.65 | 1440 | 936 | 9.6 | 7.8 | 50.4558 | YES | 1205
14 | 0.64 | 1440 | 921.6 | 9.6 | 7.8 | 50.3981 | YES | 1190
15 | 0.79 | 1440 | 1137.6 | 9.6 | 7.8 | 51.2717 | YES | 1620
16 | 0.71 | 1440 | 1022.4 | 9.6 | 7.8 | 50.8038 | YES | 1400
17 | 0.4 | 1440 | 576 | 9.3 | 7.8 | 50.0257 | YES | 860
18 | 0.62 | 1440 | 892.8 | 9.7 | 7.8 | 49.9479 | YES | 1155
19 | 0.68 | 1440 | 979.2 | 9.7 | 7.8 | 50.292 | YES | 1048
20 | 0.79 | 1440 | 1137.6 | 9.5 | 7.8 | 51.6163 | YES | 1292
21 | 0.84 | 1440 | 1209.6 | 11.1 | 7.8 | 46.6578 | YES | 1375
22 | 0.91 | 1440 | 1310.4 | 10.8 | 7.8 | 47.9781 | YES | 1105
23 | 0.99 | 1440 | 1425.6 | 13.4 | 7.8 | 40.6887 | YES | 1705
24 | 0.98 | 1440 | 1411.2 | 12.8 | 7.8 | 42.2915 | YES | 1830
25 | 1.02 | 1440 | 1468.8 | 13.1 | 7.8 | 41.6472 | YES | 1765
26 | 0.97 | 1440 | 1396.8 | 13.3 | 7.8 | 40.8668 | YES | 1810
27 | 1.02 | 1440 | 1468.8 | 11.6 | 7.8 | 46.0681 | YES | 1689
28 | 1.04 | 1440 | 1497.6 | 11.4 | 7.8 | 46.7895 | YES | 1796
29 | 1 | 1440 | 1440 | 12.8 | 7.8 | 42.3873 | YES | 3035
30 | 0.92 | 1440 | 1324.8 | 11.7 | 7.8 | 45.248 | YES | 1683
31 | 0.91 | 1440 | 1310.4 | 10.3 | 7.8 | 49.6041 | YES | 1742
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2