## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-06-01
System Name: | Barclay Meadows Water Co-Op |  |  | ID#: 39 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0
2 |  |  |  | 0
3 |  |  |  | 0
4 |  |  |  | 0
5 |  |  |  | 0
6 |  |  |  | 0
7 |  |  |  | 0
8 |  |  |  | 0
9 |  |  |  | 0
10 |  |  |  | 0
11 |  |  |  | 0
12 |  |  |  | 0
13 |  |  |  | 0
14 |  |  |  | 0
15 |  |  |  | 0
16 |  |  |  | 0
17 |  |  |  | 0
18 |  |  |  | 0
19 |  |  |  | 0
20 |  |  |  | 0
21 |  |  |  | 0
22 |  |  |  | 0
23 |  |  |  | 0
24 |  |  |  | 0
25 |  |  |  | 0
26 |  |  |  | 0
27 |  |  |  | 0
28 |  |  |  | 0
29 |  |  |  | 0
30 |  |  |  | 0
31
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Robert Riecke
[5 empty] | SIGNATURE: |  |  | 2022-06-01
[5 empty] | PHONE #: ( 541 ) 528-3257 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Barclay Meadows Water Co-Op |  | ID#: 39 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.94 | 1440 | 1353.6 | 12.4 | 8 | 46.4631 | YES | 1660
2 | 0.98 | 1440 | 1411.2 | 13.3 | 8 | 44.0373 | YES | 1460
3 | 0.92 | 1440 | 1324.8 | 12.9 | 8 | 44.9132 | YES | 2050
4 | 0.9 | 1440 | 1296 | 12.8 | 8 | 45.1094 | YES | 1230
5 | 0.92 | 1440 | 1324.8 | 13.1 | 8 | 44.3226 | YES | 1570
6 | 0.93 | 1440 | 1339.2 | 13.5 | 8.1 | 44.8315 | YES | 1185
7 | 0.79 | 1440 | 1137.6 | 14.2 | 8.1 | 42.1285 | YES | 1105
8 | 0.68 | 1440 | 979.2 | 13.9 | 8.1 | 42.4427 | YES | 880
9 | 0.64 | 1440 | 921.6 | 14 | 8.1 | 41.972 | YES | 1300
10 | 0.74 | 1440 | 1065.6 | 13.8 | 8.1 | 43.0157 | YES | 1680
11 | 0.77 | 1440 | 1108.8 | 14.6 | 8.2 | 42.4682 | YES | 1850
12 | 0.71 | 1440 | 1022.4 | 13.8 | 8.1 | 42.87 | YES | 1940
13 | 0.63 | 1440 | 907.2 | 12.9 | 8.1 | 45.0924 | YES | 1985
14 | 0.63 | 1440 | 907.2 | 13.7 | 8.1 | 42.7661 | YES | 1402
15 | 0.83 | 1440 | 1195.2 | 12.6 | 8.1 | 47.0473 | YES | 2730
16 | 0.92 | 1440 | 1324.8 | 13.3 | 8.1 | 45.3774 | YES | 2765
17 | 1.19 | 1440 | 1713.6 | 11.8 | 8.1 | 51.5595 | YES | 1970
18 | 1.21 | 1440 | 1742.4 | 13.5 | 8.2 | 48.0034 | YES | 2210
19 | 1.02 | 1440 | 1468.8 | 13.9 | 8.3 | 47.4698 | YES | 1716
20 | 1.26 | 1440 | 1814.4 | 13.9 | 8.3 | 48.7735 | YES | 5620
21 | 1.28 | 1440 | 1843.2 | 13.9 | 8.3 | 48.8837 | YES | 3135
22 | 1.4 | 1440 | 2016 | 12.8 | 8.3 | 53.2832 | YES | 2995
23 | 1.33 | 1440 | 1915.2 | 13.8 | 8.3 | 49.4862 | YES | 1870
24 | 1.4 | 1440 | 2016 | 12.7 | 8.3 | 53.6359 | YES | 1440
25 | 1.38 | 1440 | 1987.2 | 15.3 | 8.4 | 46.7538 | YES | 2125
26 | 1.41 | 1440 | 2030.4 | 16.7 | 8.6 | 46.0236 | YES | 2645
27 | 1.35 | 1440 | 1944 | 18.2 | 9 | 47.9468 | YES | 3270
28 | 1.28 | 1440 | 1843.2 | 14.9 | 9 | 59.1453 | YES | 950
29 | 1.35 | 1440 | 1944 | 15.3 | 9.3 | 64.7967 | YES | 1930
30 | 1.35 | 1440 | 1944 | 14 | 9.4 | 73.2065 | YES | 1260
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2