## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-07-22
System Name: | Barclay Meadows Water Co-Op |  |  | ID#: 39 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0
2 |  |  |  | 0
3 |  |  |  | 0
4 |  |  |  | 0
5 |  |  |  | 0
6 |  |  |  | 0
7 |  |  |  | 0
8 |  |  |  | 0
9 |  |  |  | 0
10 |  |  |  | 0
11 |  |  |  | 0
12 |  |  |  | 0
13 |  |  |  | 0
14 |  |  |  | 0
15 |  |  |  | 0
16 |  |  |  | 0
17 |  |  |  | 0
18 |  |  |  | 0
19 |  |  |  | 0
20 |  |  |  | 0
21 |  |  |  | 0
22 |  |  |  | 0
23 |  |  |  | 0
24 |  |  |  | 0
25 |  |  |  | 0
26 |  |  |  | 0
27 |  |  |  | 0
28 |  |  |  | 0
29 |  |  |  | 0
30 |  |  |  | 0
31 |  |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Robert Riecke
[5 empty] | SIGNATURE: |  |  | DATE:July 2022
[5 empty] | PHONE #: ( 541 ) 528-3257 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Barclay Meadows Water Co-Op |  | ID#: 39 |  | Month/Year: | 2022-07-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.39 | 1440 | 2001.6 | 16.7 | 9.4 | 61.568 | YES | 2665
2 | 1.42 | 1440 | 2044.8 | 14.7 | 9.5 | 73.086 | YES | 2330
3 | 1.4 | 1440 | 2016 | 15.5 | 9.5 | 69.1857 | YES | 2395
4 | 1.4 | 1440 | 2016 | 14.7 | 9.6 | 75.6327 | YES | 3070
5 | 1.29 | 1440 | 1857.6 | 15.6 | 9.5 | 67.8881 | YES | 1540
6 | 1.25 | 1440 | 1800 | 14.3 | 9.5 | 73.6148 | YES | 1000
7 | 1.15 | 1440 | 1656 | 17.1 | 7.3 | 26.9154 | YES | 1810
8 | 1.13 | 1440 | 1627.2 | 14.1 | 7.5 | 35.3293 | YES | 2070
9 | 1.1 | 1440 | 1584 | 17 | 7.5 | 29.02 | YES | 2170
10 | 1.17 | 1440 | 1684.8 | 14.7 | 7.4 | 32.8634 | YES | 1970
11 | 1.14 | 1440 | 1641.6 | 17.2 | 7.5 | 28.7657 | YES | 2492
12 | 1.18 | 1440 | 1699.2 | 15.3 | 7.5 | 32.8032 | YES | 4380
13 | 1.26 | 1440 | 1814.4 | 13.9 | 7.7 | 39.116 | YES | 3880
14 | 1.28 | 1440 | 1843.2 | 15 | 7 | 28.1231 | YES | 3370
15 | 1.34 | 1440 | 1929.6 | 14.6 | 7.7 | 37.6801 | YES | 3680
16 | 1.35 | 1440 | 1944 | 14.8 | 7.7 | 37.2251 | YES | 4400
17 | 2.04 | 1440 | 2937.6 | 13.6 | 7.8 | 45.217 | YES | 6400
18 | 1.52 | 1440 | 2188.8 | 13.2 | 7.7 | 42.1985 | YES | 2546
19 | 1.38 | 1440 | 1987.2 | 13.8 | 7.7 | 39.9153 | YES | 2546
20 | 1.25 | 1440 | 1800 | 14.7 | 7.6 | 35.7079 | YES | 2546
21 | 1.19 | 1440 | 1713.6 | 14.6 | 7.7 | 37.0444 | YES | 1430
22 | 1.14 | 1440 | 1641.6 | 14.7 | 7.7 | 36.591 | YES | 1760
23 | 1.15 | 1440 | 1656 | 15.9 | 7.6 | 32.5944 | YES | 1650
24 | 1.14 | 1440 | 1641.6 | 14.3 | 7.7 | 37.5763 | YES | 4760
25 | 1.14 | 1440 | 1641.6 | 14.2 | 7.7 | 37.8267 | YES | 4920
26 | 1.08 | 1440 | 1555.2 | 14.5 | 7.6 | 35.4941 | YES | 4290
27 | 1.07 | 1440 | 1540.8 | 15.1 | 7.5 | 32.8297 | YES | 3140
28 | 1.02 | 1440 | 1468.8 | 18.1 | 7.6 | 27.7277 | YES | 3050
29 | 0.92 | 1440 | 1324.8 | 19.2 | 7.5 | 24.5329 | YES | 4150
30 | 0.98 | 1440 | 1411.2 | 17.8 | 7.5 | 27.1334 | YES | 28.95
31 | 1.16 | 1440 | 1670.4 | 18.3 | 7.5 | 26.7856 | YES | 3320
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2