## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-09-01
System Name: | Barclay Meadows Water Co-Op |  |  | ID#: 39 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0
2 |  |  |  | 0
3 |  |  |  | 0
4 |  |  |  | 0
5 |  |  |  | 0
6 |  |  |  | 0
7 |  |  |  | 0
8 |  |  |  | 0
9 |  |  |  | 0
10 |  |  |  | 0
11 |  |  |  | 0
12 |  |  |  | 0
13 |  |  |  | 0
14 |  |  |  | 0
15 |  |  |  | 0
16 |  |  |  | 0
17 |  |  |  | 0
18 |  |  |  | 0
19 |  |  |  | 0
20 |  |  |  | 0
21 |  |  |  | 0
22 |  |  |  | 0
23 |  |  |  | 0
24 |  |  |  | 0
25 |  |  |  | 0
26 |  |  |  | 0
27 |  |  |  | 0
28 |  |  |  | 0
29 |  |  |  | 0
30 |  |  |  | 0
31 |  |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Robert Riecke
[5 empty] | SIGNATURE: |  |  | DATE:Sept 2022
[5 empty] | PHONE #: ( 541 ) 528-3257 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Barclay Meadows Water Co-Op |  | ID#: 39 |  | Month/Year: | 2022-09-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.76 | 1440 | 1094.4 | 14.4 | 7.7 | 35.7521 | YES | 2465
2 | 0.84 | 1440 | 1209.6 | 14.4 | 7.7 | 36.0783 | YES | 5540
3 | 0.72 | 1440 | 1036.8 | 18.6 | 7.6 | 25.9099 | YES | 3110
4 | 0.94 | 1440 | 1353.6 | 14 | 7.7 | 37.4728 | YES | 2220
5 | 0.99 | 1440 | 1425.6 | 15.7 | 7.7 | 33.658 | YES | 7050
6 | 0.85 | 1440 | 1224 | 14.2 | 7.8 | 37.9781 | YES | 7135
7 | 1.04 | 1440 | 1497.6 | 13.3 | 7.8 | 41.1919 | YES | 5895
8 | 1.1 | 1440 | 1584 | 12.7 | 7.8 | 43.1544 | YES | 7365
9 | 0.92 | 1440 | 1324.8 | 13.7 | 7.8 | 39.5722 | YES | 6145
10 | 0.89 | 1440 | 1281.6 | 14.6 | 7.7 | 35.8044 | YES | 5615
11 | 0.81 | 1440 | 1166.4 | 15 | 7.7 | 34.5491 | YES | 4885
12 | 0.95 | 1440 | 1368 | 14.4 | 7.7 | 36.5315 | YES | 10195
13 | 0.89 | 1440 | 1281.6 | 15 | 7.7 | 34.8646 | YES | 4555
14 | 0.87 | 1440 | 1252.8 | 14.9 | 7.7 | 35.0176 | YES | 3930
15 | 0.85 | 1440 | 1224 | 14.9 | 7.7 | 34.9382 | YES | 3750
16 | 0.85 | 1440 | 1224 | 13.8 | 7.7 | 37.5882 | YES | 4260
17 | 0.85 | 1440 | 1224 | 14.7 | 7.7 | 35.406 | YES | 6710
18 | 0.94 | 1440 | 1353.6 | 13.3 | 7.8 | 40.7282 | YES | 4125
19 | 0.96 | 1440 | 1382.4 | 13.5 | 7.8 | 40.2827 | YES | 4120
20 | 1.04 | 1440 | 1497.6 | 13.7 | 7.8 | 40.1138 | YES | 4640
21 | 1.06 | 1440 | 1526.4 | 13.4 | 7.8 | 41.0125 | YES | 3880
22 | 1.11 | 1440 | 1598.4 | 15 | 7.8 | 37.0907 | YES | 4360
23 | 1.08 | 1440 | 1555.2 | 17 | 7.7 | 31.1827 | YES | 4345
24 | 1.09 | 1440 | 1569.6 | 12.3 | 7.9 | 45.924 | YES | 4700
25 | 1.1 | 1440 | 1584 | 12.3 | 7.9 | 45.9762 | YES | 5100
26 | 1.08 | 1440 | 1555.2 | 15.8 | 7.8 | 35.0502 | YES | 5920
27 | 1.06 | 1440 | 1526.4 | 13.8 | 7.8 | 39.9389 | YES | 4280
28 | 0.96 | 1440 | 1382.4 | 14.4 | 7.8 | 37.9474 | YES | 4525
29 | 0.82 | 1440 | 1180.8 | 15 | 7.8 | 35.8899 | YES | 4770
30 | 0.43 | 1440 | 619.2 | 14.2 | 7.6 | 33.6318 | YES | 3945
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2