## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-01-23
System Name: | Barclay Meadows Water Co-Op |  |  | ID#: 39 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0
2 |  |  |  | 0
3 |  |  |  | 0
4 |  |  |  | 0
5 |  |  |  | 0
6 |  |  |  | 0
7 |  |  |  | 0
8 |  |  |  | 0
9 |  |  |  | 0
10 |  |  |  | 0
11 |  |  |  | 0
12 |  |  |  | 0
13 |  |  |  | 0
14 |  |  |  | 0
15 |  |  |  | 0
16 |  |  |  | 0
17 |  |  |  | 0
18 |  |  |  | 0
19 |  |  |  | 0
20 |  |  |  | 0
21 |  |  |  | 0
22 |  |  |  | 0
23 |  |  |  | 0
24 |  |  |  | 0
25 |  |  |  | 0
26 |  |  |  | 0
27 |  |  |  | 0
28 |  |  |  | 0
29 |  |  |  | 0
30 |  |  |  | 0
31 |  |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Robert Riecke
[5 empty] | SIGNATURE: |  |  | DATE:01/02/2023
[5 empty] | PHONE #: ( 541 ) 528-3257 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Barclay Meadows Water Co-Op |  | ID#: 39 |  | Month/Year: | 2023-01-23 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.71 | 1440 | 1022.4 | 6.1 | 7.9 | 66.7441 | YES | 1893
2 | 0.75 | 1440 | 1080 | 6.8 | 7.9 | 63.928 | YES | 1893
3 | 0.78 | 1440 | 1123.2 | 7.1 | 7.9 | 62.8544 | YES | 2238
4 | 0.66 | 1440 | 950.4 | 7.5 | 7.9 | 60.32 | YES | 1803
5 | 0.68 | 1440 | 979.2 | 8.3 | 7.9 | 57.271 | YES | 1620
6 | 0.61 | 1440 | 878.4 | 9.8 | 7.9 | 51.3565 | YES | 2210
7 | 0.65 | 1440 | 936 | 9.2 | 7.8 | 51.8253 | YES | 2210
8 | 0.69 | 1440 | 993.6 | 9 | 7.8 | 52.7672 | YES | 2150
9 | 0.54 | 1440 | 777.6 | 9 | 7.9 | 53.755 | YES | 2175
10 | 0.66 | 1440 | 950.4 | 7 | 7.9 | 62.4048 | YES | 1465
11 | 0.7 | 1440 | 1008 | 8.5 | 7.8 | 54.6342 | YES | 2205
12 | 0.74 | 1440 | 1065.6 | 10.1 | 7.8 | 49.3034 | YES | 2040
13 | 0.81 | 1440 | 1166.4 | 10.7 | 7.8 | 47.7513 | YES | 2445
14 | 0.73 | 1440 | 1051.2 | 10.1 | 7.8 | 49.2471 | YES | 515
15 | 0.76 | 1440 | 1094.4 | 9.8 | 7.8 | 50.4165 | YES | 2360
16 | 0.7 | 1440 | 1008 | 8 | 7.9 | 58.581 | YES | 2110
17 | 0.63 | 1440 | 907.2 | 8 | 7.9 | 58.1075 | YES | 1983
18 | 0.39 | 1440 | 561.6 | 9.1 | 7.9 | 52.4817 | YES | 1237
19 | 0.56 | 1440 | 806.4 | 9 | 7.9 | 53.8789 | YES | 1978
20 | 0.74 | 1440 | 1065.6 | 8.7 | 7.9 | 56.1326 | YES | 3182
21 | 0.83 | 1440 | 1195.2 | 5 | 7.9 | 72.994 | YES | 1570
22 | 1.02 | 1440 | 1468.8 | 6.2 | 7.9 | 68.7412 | YES | 1850
23 | 1.18 | 1440 | 1699.2 | 4.8 | 7.9 | 77.1253 | YES | 1965
24 | 1.15 | 1440 | 1656 | 5.2 | 7.9 | 74.7628 | YES | 1860
25 | 1.28 | 1440 | 1843.2 | 6.7 | 7.9 | 68.4837 | YES | 1385
26 | 1.41 | 1440 | 2030.4 | 7.1 | 7.9 | 67.6571 | YES | 1770
27 | 1.5 | 1440 | 2160 | 7.3 | 7.9 | 67.445 | YES | 1270
28 | 1.54 | 1440 | 2217.6 | 8.1 | 7.9 | 64.1583 | YES | 3480
29 | 1.56 | 1440 | 2246.4 | 4.3 | 8 | 86.6569 | YES | 3205
30 | 1.28 | 1440 | 1843.2 | 4 | 8 | 85.5842 | YES | 3935
31 | 1.21 | 1440 | 1742.4 | 3.5 | 8 | 87.8732 | YES | 5020
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2