## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-03-01
System Name: | Barclay Meadows Water Co-Op |  |  | ID#: 39 |  |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0
2 |  |  |  | 0
3 |  |  |  | 0
4 |  |  |  | 0
5 |  |  |  | 0
6 |  |  |  | 0
7 |  |  |  | 0
8 |  |  |  | 0
9 |  |  |  | 0
10 |  |  |  | 0
11 |  |  |  | 0
12 |  |  |  | 0
13 |  |  |  | 0
14 |  |  |  | 0
15 |  |  |  | 0
16 |  |  |  | 0
17 |  |  |  | 0
18 |  |  |  | 0
19 |  |  |  | 0
20 |  |  |  | 0
21 |  |  |  | 0
22 |  |  |  | 0
23 |  |  |  | 0
24 |  |  |  | 0
25 |  |  |  | 0
26 |  |  |  | 0
27 |  |  |  | 0
28 |  |  |  | 0
29 |  |  |  | 0
30 |  |  |  | 0
31 |  |  |  | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Robert Riecke
[5 empty] | SIGNATURE: |  |  | 2023-03-01
[5 empty] | PHONE #: ( 541 ) 528-3257 |  |  | CERT #:
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Barclay Meadows Water Co-Op |  | ID#: 39 |  | Month/Year: | 2023-03-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.07 | 1440 | 1540.8 | 3.5 | 8 | 86.4223 | YES | 2420
2 | 1.04 | 1440 | 1497.6 | 4.9 | 8 | 78.1603 | YES | 2995
3 | 1.1 | 1440 | 1584 | 4.9 | 7.9 | 75.8752 | YES | 2940
4 | 1.15 | 1440 | 1656 | 5.6 | 7.9 | 72.7333 | YES | 3640
5 | 1.17 | 1440 | 1684.8 | 5.2 | 7.9 | 74.9393 | YES | 4625
6 | 1.12 | 1440 | 1612.8 | 4.6 | 7.9 | 77.6446 | YES | 5045
7 | 1.08 | 1440 | 1555.2 | 6.6 | 7.9 | 67.3565 | YES | 3772
8 | 1.21 | 1440 | 1742.4 | 5.6 | 7.9 | 73.2489 | YES | 3630
9 | 1.25 | 1440 | 1800 | 5.9 | 7.9 | 72.0924 | YES | 3380
10 | 1.24 | 1440 | 1785.6 | 4.6 | 7.9 | 78.754 | YES | 3720
11 | 1.25 | 1440 | 1800 | 6.4 | 7.9 | 69.6604 | YES | 3550
12 | 0.91 | 1440 | 1310.4 | 7.5 | 8 | 64.3954 | YES | 4195
13 | 1.24 | 1440 | 1785.6 | 6.8 | 7.9 | 67.6983 | YES | 3360
14 | 1.26 | 1440 | 1814.4 | 5.9 | 7.9 | 72.1773 | YES | 3430
15 | 1.16 | 1440 | 1670.4 | 7.3 | 7.9 | 64.815 | YES | 4005
16 | 1.13 | 1440 | 1627.2 | 6.1 | 7.8 | 67.6 | YES | 3860
17 | 1.2 | 1440 | 1728 | 5.2 | 7.8 | 72.4974 | YES | 3750
18 | 1.36 | 1440 | 1958.4 | 7.3 | 7.8 | 63.9788 | YES | 3580
19 | 1.38 | 1440 | 1987.2 | 8.8 | 7.8 | 57.9166 | YES | 3425
20 | 1.28 | 1440 | 1843.2 | 8.6 | 7.8 | 58.0295 | YES | 3210
21 | 1.14 | 1440 | 1641.6 | 7.6 | 7.8 | 61.0993 | YES | 2195
22 | 1.28 | 1440 | 1843.2 | 7.5 | 7.8 | 62.5271 | YES | 2515
23 | 1.17 | 1440 | 1684.8 | 7.6 | 7.8 | 61.3129 | YES | 2550
24 | 1.13 | 1440 | 1627.2 | 7.4 | 7.8 | 61.8635 | YES | 2330
25 | 0.99 | 1440 | 1425.6 | 7.6 | 7.8 | 60.0431 | YES | 2925
26 | 1.16 | 1440 | 1670.4 | 7.2 | 7.8 | 62.9307 | YES | 2855
27 | 1.22 | 1440 | 1756.8 | 7.5 | 7.8 | 62.0916 | YES | 2640
28 | 1.33 | 1440 | 1915.2 | 7.6 | 7.8 | 62.4659 | YES | 3115
29 | 1.25 | 1440 | 1800 | 7.6 | 7.8 | 61.8865 | YES | 3200
30 | 1.09 | 1440 | 1569.6 | 7.4 | 7.9 | 63.8505 | YES | 2615
31 | 1.15 | 1440 | 1656 | 7.1 | 7.9 | 65.6291 | YES | 2930
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2