## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | JACKSON
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2021-08-01
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
2 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
3 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
4 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
5 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04
6 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
7 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
8 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
9 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
10 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
11 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
12 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.041
13 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
14 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.06
15 | 0.05 | 0.05 | 0.04 | 0.03 | 0.03 | 0.03 | 0.05
16 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05
17 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
18 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
19 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
20 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
21 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
22 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
23 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
24 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03 | 0.04
25 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
26 | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.04
27 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
28 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05
29 | 0.04 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.04
30 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.03 | 0.04
31 | 0.03 | 0.03 | 0.04 | 0.04 | 0.03 | 0.03 | 0.04
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Alistair Andre
[5 empty] | SIGNATURE: |  |  | 2021-09-01
[5 empty] | PHONE #: (541) - 488 - 5345 |  |  | CERT #: T-08640
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP : TP - | A
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 | 2021-08-01 |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 - 1610 | 0.87 | 96 | 83.52 | 21 | 7.4 | 20.814 | YES | 2600
2 - 1546 | 0.86 | 86 | 73.96 | 21 | 7.4 | 20.79 | YES | 2811
3 - 0009 | 0.77 | 86 | 66.22 | 21 | 7.4 | 20.5753 | YES | 2825
4 - 0633 | 0.95 | 91 | 86.45 | 21 | 7.4 | 21.007 | YES | 2738
5 - 0738 | 1.03 | 93 | 95.79 | 21 | 7.4 | 21.2016 | YES | 2635
6 - 1041 | 0.97 | 96 | 92.8 | 21 | 7.4 | 21.0555 | YES | 2570
7 - 1941 | 0.91 | 96 | 87.36 | 21 | 7.4 | 20.9 | YES | 2557
8 - 2130 | 1.01 | 93 | 93.93 | 21 | 7.4 | 21.1528 | YES | 2635
9 - 2016 | 0.93 | 93 | 86.49 | 21 | 7.4 | 20.9586 | YES | 2640
10 - 0054 | 0.94 | 93 | 87.42 | 21 | 7.4 | 20.9827 | YES | 2613
11 - 0253 | 0.82 | 96 | 78.72 | 21 | 7.4 | 20.6943 | YES | 2589
12 - 1809 | 0.97 | 98 | 95.06 | 21 | 7.4 | 21.0555 | YES | 2474
13 - 1156 | 1.04 | 98 | 101.92 | 21 | 7.4 | 21.2261 | YES | 2502
14 - 1659 | 0.91 | 96 | 87.36 | 21 | 7.4 | 20.9103 | YES | 2604
15 - 0950 | 0.96 | 93 | 89.28 | 21 | 7.4 | 21.0312 | YES | 2613
16 - 0113 | 0.86 | 101 | 86.86 | 21 | 7.4 | 20.79 | YES | 2397
17 - 1611 | 0.88 | 101 | 88.88 | 21 | 7.4 | 20.838 | YES | 2433
18 - 0933 | 1.13 | 101 | 114.13 | 21 | 7.4 | 21.4474 | YES | 2418
19 - 1922 | 0.89 | 107 | 95.23 | 21 | 7.4 | 20.8621 | YES | 2275
20 - 2116 | 0.86 | 107 | 92.02 | 20 | 7.4 | 22.2411 | YES | 2291
21 - 0458 | 0.86 | 107 | 92.02 | 20 | 7.4 | 22.2411 | YES | 2275
22 - 0407 | 0.81 | 111 | 89.91 | 20 | 7.4 | 22.1135 | YES | 2188
23 - 1151 | 0.99 | 114 | 112.86 | 20 | 7.4 | 22.5762 | YES | 2136
24 - 1554 | 0.91 | 101 | 91.91 | 20 | 7.4 | 22.3694 | YES | 2424
25 - 0126 | 0.88 | 101 | 88.88 | 19 | 7.4 | 23.8443 | YES | 2441
26 - 0943 | 0.96 | 111 | 106.56 | 19 | 7.4 | 24.0642 | YES | 2252
27 - 1704 | 0.95 | 111 | 105.45 | 19 | 7.4 | 24.0366 | YES | 2204
28 - 0614 | 1.03 | 111 | 114.33 | 19 | 7.4 | 24.2583 | YES | 2237
29 - 1538 | 0.99 | 114 | 112.86 | 19 | 7.4 | 24.1472 | YES | 2183
30 - 0224 | 0.87 | 111 | 96.57 | 19 | 7.4 | 23.8169 | YES | 2208
31 - 0643 | 0.91 | 111 | 101.01 | 19 | 7.4 | 23.9265 | YES | 2192
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2