## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | JACKSON
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-08-01
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05
2 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
3 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
4 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
5 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
6 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
7 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
8 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05
9 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.03 | 0.05
10 | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.05
11 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
12 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03 | 0.04
13 | 0.04 | 0.04 | 0.04 | 0.03 | 0.04 | 0.04 | 0.04
14 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05
15 | 0.03 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04
16 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06
17 | 0.04 | 0.05 | 0.04 | 0.04 | 0.03 | 0.03 | 0.06
18 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.05
19 | 0.05 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05
20 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
21 | 0.03 | 0.03 | 0.03 | 0.04 | 0.05 | 0.03 | 0.05
22 | 0.04 | 0.04 | 0.04 | 0.03 | 0.03 | 0.04 | 0.04
23 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03 | 0.05
24 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
25 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04
26 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.041
27 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
28 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
29 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04
30 | 0.03 | 0.04 | 0.04 | 0.03 | 0.03 | 0.03 | 0.04
31 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.03 | 0.04
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Alistair Andre
[5 empty] | SIGNATURE: |  |  | DATE:9/6/2022
[5 empty] | PHONE #: (541) - 488 - 5345 |  |  | CERT #: T-08640
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP : TP - | A
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 | Month/Year: |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 - 0328 | 0.87 | 63 | 54.81 | 21 | 7.7 | 23.2881 | YES | 3876
2 - 0747 | 0.92 | 62 | 57.04 | 20 | 7.6 | 24.133 | YES | 3950
3 - 0946 | 0.95 | 84 | 79.8 | 20 | 7.6 | 24.2162 | YES | 2886
4 - 0206 | 0.86 | 96 | 82.56 | 22 | 7.6 | 20.9462 | YES | 2559
5 - 1733 | 0.92 | 111 | 102.12 | 22 | 7.7 | 21.8969 | YES | 2221
6 - 0623 | 0.93 | 111 | 103.23 | 21 | 7.6 | 22.5888 | YES | 2205
7 - 1022 | 0.89 | 111 | 98.79 | 20 | 7.6 | 24.0501 | YES | 2228
8 - 1532 | 0.86 | 98 | 84.28 | 23 | 7.4 | 18.1561 | YES | 2484
9 - 0311 | 0.78 | 98 | 76.44 | 23 | 7.4 | 17.9884 | YES | 2527
10 - 0000 | 0.81 | 101 | 81.81 | 21 | 7.5 | 21.4603 | YES | 2411
11 - 0231 | 0.86 | 101 | 86.86 | 21 | 7.4 | 20.79 | YES | 2423
12 - 0832 | 1.01 | 114 | 115.14 | 20 | 7.3 | 21.797 | YES | 2159
13 - 2303 | 0.88 | 114 | 100.32 | 21 | 7.4 | 20.838 | YES | 2129
14 - 1046 | 0.9 | 114 | 102.6 | 20 | 7.3 | 21.5225 | YES | 2138
15 - 1425 | 0.97 | 111 | 107.67 | 21 | 7.4 | 21.0555 | YES | 2210
16 - 1616 | 0.86 | 107 | 92.02 | 23 | 7.3 | 17.4834 | YES | 2265
17 - 0513 | 0.76 | 107 | 81.32 | 22 | 7.3 | 18.4969 | YES | 2277
18 - 1144 | 0.88 | 107 | 94.16 | 21 | 7.3 | 20.0703 | YES | 2285
19 - 1112 | 0.9 | 114 | 102.6 | 21 | 7.3 | 20.1167 | YES | 2141
20 - 1424 | 0.88 | 107 | 94.16 | 22 | 7.3 | 18.7558 | YES | 2280
21 - 2059 | 0.74 | 101 | 74.74 | 24 | 7.2 | 15.5049 | YES | 2414
22 - 1329 | 0.92 | 91 | 83.72 | 21 | 7.3 | 20.1632 | YES | 2697
23 - 1145 | 0.87 | 91 | 79.17 | 20 | 7.3 | 21.4483 | YES | 2684
24 - 0001 | 0.77 | 93 | 71.61 | 23 | 7.3 | 17.3015 | YES | 2627
25 - 0354 | 0.86 | 96 | 82.56 | 22 | 7.2 | 18.02 | YES | 2595
26 - 0251 | 0.81 | 93 | 75.33 | 23 | 7.2 | 16.7369 | YES | 2645
27 - 0456 | 0.85 | 93 | 79.05 | 22 | 7.2 | 17.9991 | YES | 2608
28 - 0812 | 1.01 | 93 | 93.93 | 20 | 7.2 | 20.9952 | YES | 2620
29 - 1112 | 0.96 | 93 | 89.28 | 20 | 7.2 | 20.8745 | YES | 2614
30 - 0730 | 0.97 | 72 | 69.84 | 21 | 7.2 | 19.532 | YES | 3422
31 - 0539 | 0.99 | 77 | 76.23 | 21 | 7.2 | 19.5772 | YES | 3175
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2