## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | JACKSON
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-07-01
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
2 | 0.03 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
3 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
4 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03
5 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
6 | 0.02 | 0.03 | 0.03 | 0.03 | 0.02 | 0.02 | 0.04
7 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03
8 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
9 | 0.02 | 0.02 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03
10 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
11 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
12 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
13 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
14 | 0.03 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03
15 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
16 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.04
17 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.06
18 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.05
19 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.1
20 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03 | 0.05
21 | 0.03 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02 | 0.03
22 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
23 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.05
24 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.02 | 0.03
25 | 0.03 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02 | 0.03
26 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.02 | 0.03
27 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
28 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03
29 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.02 | 0.03
30 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
31 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Alistair Andre
[5 empty] | SIGNATURE: |  |  | DATE: 8/1/2024
[5 empty] | PHONE #: (541) - 488 - 5345 |  |  | CERT #: T-08640
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP : TP - | A
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 | Month/Year: |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 - 16 14 | 0.96 | 64 | 61.44 | 13 | 7.6 | 38.6831 | YES | 3803
2 - 19 15 | 0.89 | 61 | 54.29 | 13 | 7.6 | 38.3773 | YES | 4041
3 - 11 35 | 1 | 60 | 60 | 13 | 7.4 | 36.0953 | YES | 4065
4 - 02 31 | 0.95 | 61 | 57.95 | 13 | 7.4 | 35.891 | YES | 4009
5 - 14 05 | 1.01 | 59 | 59.59 | 14 | 7.6 | 36.4033 | YES | 4161
6 - 22 17 | 0.83 | 58 | 48.14 | 15 | 7.5 | 32.1589 | YES | 4238
7 - 09 48 | 1.04 | 57 | 59.28 | 14 | 7.4 | 33.9262 | YES | 4290
8 - 03 05 | 0.91 | 57 | 51.87 | 15 | 7.3 | 30.1356 | YES | 4284
9 - 08 27 | 0.92 | 57 | 52.44 | 14 | 7.3 | 32.251 | YES | 4297
10 - 05 32 | 0.92 | 57 | 52.5 | 15 | 7.4 | 31.3 | YES | 4320
11 - 13 07 | 0.95 | 57 | 54.2 | 15 | 7.6 | 33.8 | YES | 4303
12 - 10 14 | 0.85 | 55 | 46.75 | 15 | 7.5 | 32.2322 | YES | 4425
13 - 03 15 | 0.9 | 55 | 49.5 | 15 | 7.5 | 32.4161 | YES | 4450
14 - 03 09 | 0.89 | 56 | 49.84 | 16 | 7.4 | 29.1872 | YES | 4376
15 - 20 04 | 0.87 | 56 | 48.72 | 16 | 7.4 | 29.1207 | YES | 4242
16 - 14 56 | 0.89 | 58 | 51.62 | 16 | 7.5 | 30.2902 | YES | 4242
17 - 13 52 | 0.98 | 54 | 52.92 | 17 | 7.5 | 28.6252 | YES | 4563
18 - 03 59 | 1.06 | 54 | 57.24 | 16 | 7.5 | 30.8827 | YES | 4490
19 - 12 24 | 0.98 | 55 | 53.9 | 16 | 7.5 | 30.6025 | YES | 4434
20 - 18 33 | 1.09 | 53 | 57.77 | 16 | 7.5 | 30.9884 | YES | 4619
21 - 15 11 | 0.95 | 54 | 51.3 | 17 | 7.4 | 27.4869 | YES | 4606
22 - 01 27 | 0.94 | 54 | 50.76 | 17 | 7.3 | 26.4531 | YES | 4565
23 - 20 44 | 1.02 | 56 | 57.12 | 17 | 7.4 | 27.7077 | YES | 4359
24 - 23 10 | 0.88 | 55 | 48.4 | 17 | 7.4 | 27.2679 | YES | 4458
25 - 05 41 | 0.9 | 55 | 49.5 | 17 | 7.3 | 26.3323 | YES | 4421
26 - 01 52 | 0.95 | 59 | 56.05 | 18 | 7.4 | 25.7057 | YES | 4167
27 - 21 33 | 0.97 | 58 | 56.26 | 18 | 7.4 | 25.7647 | YES | 4210
28 - 14 35 | 1.04 | 56 | 58.24 | 18 | 7.5 | 26.9567 | YES | 4363
29 - 00 44 | 0.91 | 57 | 51.87 | 18 | 7.3 | 24.652 | YES | 4329
30 - 10 38 | 0.98 | 59 | 57.8 | 18 | 7.4 | 25.7942 | YES | 4164
31 - 12 18 | 0.9 | 59 | 53.1 | 18 | 7.4 | 25.5589 | YES | 4147
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2