## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | JACKSON
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-08-01
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
2 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
3 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
4 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
5 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
6 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03
7 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03
8 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03
9 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
10 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
11 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
12 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
13 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
14 | 0.04 | 0.04 | 0.04 | 0.03 | 0.03 | 0.03 | 0.04
15 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
16 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
17 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
18 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
19 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
20 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
21 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
22 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
23 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
24 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
25 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
26 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
27 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03
28 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
29 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
30 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
31 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Alistair Andre
[5 empty] | SIGNATURE: |  |  | DATE: 9-4-2024
[5 empty] | PHONE #: (541) - 488 - 5345 |  |  | CERT #: T-08640
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP : TP - | A
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 | Month/Year: |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 - 14 05 | 1 | 56 | 56 | 18 | 7.4 | 25.8533 | YES | 4362
2 - 06 50 | 1.02 | 54 | 54.7 | 18 | 7.4 | 25.9126 | YES | 4602
3 - 00 40 | 0.97 | 54 | 52.38 | 19 | 7.4 | 24.0919 | YES | 4624
4 - 12 17 | 0.98 | 63 | 61.74 | 19 | 7.5 | 25.0362 | YES | 3919
5 - 11 57 | 0.94 | 60 | 56.4 | 19 | 7.5 | 24.9216 | YES | 4068
6 - 13 47 | 0.93 | 59 | 54.87 | 19 | 7.5 | 24.8931 | YES | 4146
7 - 13 03 | 1.04 | 56 | 58.24 | 19 | 7.4 | 24.2862 | YES | 4409
8 - 01 33 | 1.04 | 55 | 57.2 | 19 | 7.5 | 25.2089 | YES | 4462
9 - 19 18 | 0.99 | 55 | 54.45 | 19 | 7.4 | 24.1472 | YES | 4470
10 - 00 45 | 0.98 | 54 | 52.92 | 19 | 7.4 | 24.1195 | YES | 4497
11 - 11 27 | 0.99 | 60 | 59.4 | 19 | 7.4 | 24.1472 | YES | 4130
12 - 20 48 | 0.93 | 54 | 50.22 | 19 | 7.5 | 24.8931 | YES | 4535
13 - 06 50 | 1.13 | 54 | 61.02 | 19 | 7.5 | 25.4702 | YES | 4582
14 - 04 56 | 0.99 | 55 | 54.45 | 19 | 7.6 | 26.0162 | YES | 4412
15 - 07 58 | 1.04 | 60 | 62.4 | 19 | 7.4 | 24.2862 | YES | 4073
16 - 21 18 | 1.05 | 60 | 63 | 19 | 7.5 | 25.2378 | YES | 4072
17 - 05 16 | 1.06 | 60 | 63.6 | 19 | 7.5 | 25.2668 | YES | 4070
18 - 03 39 | 0.97 | 63 | 61.11 | 18 | 7.4 | 25.7647 | YES | 3868
19 - 14 29 | 0.95 | 66 | 62.7 | 18 | 7.5 | 26.6807 | YES | 3722
20 - 12 39 | 0.96 | 66 | 63.36 | 17 | 7.5 | 28.5599 | YES | 3779
21 - 08 10 | 1.05 | 66 | 69.3 | 17 | 7.4 | 27.8028 | YES | 3771
22 - 04 45 | 0.97 | 69 | 66.93 | 17 | 7.5 | 28.5925 | YES | 3554
23 - 10 49 | 0.94 | 71 | 66.74 | 17 | 7.5 | 28.4948 | YES | 3444
24 - 02 07 | 0.95 | 71 | 67.45 | 18 | 7.5 | 26.6807 | YES | 3455
25 - 14 56 | 1.03 | 74 | 76.22 | 16 | 7.6 | 31.9387 | YES | 3358
26 - 22 55 | 1.05 | 68 | 71.4 | 16 | 7.5 | 30.8475 | YES | 3580
27 - 23 34 | 0.97 | 68 | 65.96 | 16 | 7.4 | 29.4549 | YES | 3624
28 - 14 30 | 1.09 | 63 | 68.67 | 16 | 7.5 | 30.9884 | YES | 3869
29 - 00 59 | 1.02 | 64 | 65.28 | 16 | 7.5 | 30.7423 | YES | 3842
30 - 06 10 | 1.17 | 60 | 70.2 | 17 | 7.6 | 32.5 | YES | 4063
31 - 05 29 | 1.06 | 61 | 64.66 | 16 | 7.5 | 30.8827 | YES | 4036
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2