## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | JACKSON
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-09-24
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.033
2 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.034
3 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.033
4 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03
5 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.02 | 0.03
6 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
7 | 0.03 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03 | 0.03
8 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
9 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
10 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
11 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
12 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
13 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
14 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
15 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
16 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
17 | 0.03 | 0.04 | 0.04 | 0.03 | 0.03 | 0.03 | 0.04
18 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
19 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
20 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
21 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
22 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
23 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.04 | 0.05
24 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06
25 | 0.05 | 0.04 | 0.04 | 0.05 | 0.05 | 0.06 | 0.06
26 | 0.06 | 0.05 | 0.06 | 0.05 | 0.05 | 0.05 | 0.06
27 | 0.05 | 0.06 | 0.06 | 0.05 | 0.04 | 0.06 | 0.07
28 | 0.04 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05 | 0.06
29 | 0.04 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.06
30 | 0.04 | 0.04 | 0.06 | 0.06 | 0.04 | 0.05 | 0.07
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Alistair Andre
[5 empty] | SIGNATURE: |  |  | DATE: 10-3-2024
[5 empty] | PHONE #: (541) - 488 - 5345 |  |  | CERT #: T-08640
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP : TP - | A
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 | Month/Year: |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 - 05 37 | 1.08 | 64 | 69.12 | 16 | 7.6 | 32.121 | YES | 3837
2 - 10 45 | 1.02 | 64 | 65.28 | 17 | 7.6 | 29.8433 | YES | 3798
3 - 03 48 | 1.04 | 64 | 66.56 | 16 | 7.6 | 31.9751 | YES | 3817
4 - 12 16 | 1.01 | 64 | 64.64 | 16 | 7.6 | 31.866 | YES | 3794
5 - 04 21 | 1.13 | 64 | 72.32 | 16 | 7.6 | 32.3043 | YES | 3817
6 - 20 36 | 1.01 | 64 | 64.64 | 17 | 7.4 | 27.676 | YES | 3817
7 - 09 44 | 1.29 | 63 | 81.27 | 16 | 7.5 | 31.7024 | YES | 3860
8 - 21 50 | 0.81 | 63 | 51.03 | 17 | 7.4 | 27.0505 | YES | 3855
9 - 08 38 | 0.79 | 63 | 49.77 | 16 | 7.2 | 26.7892 | YES | 3870
10 - 02 16 | 1.01 | 66 | 66.66 | 17 | 7.4 | 27.676 | YES | 3777
11 - 00 45 | 0.81 | 68 | 55.08 | 17 | 7.3 | 26.0624 | YES | 3618
12 - 01 56 | 1.07 | 75 | 80.25 | 16 | 7.2 | 27.6607 | YES | 3249
13 - 13 46 | 1.09 | 71 | 77.39 | 16 | 7.4 | 29.8608 | YES | 3444
14 - 04 42 | 1.13 | 71 | 80.23 | 16 | 7.3 | 28.9047 | YES | 3443
15 - 13 22 | 1.19 | 71 | 84.49 | 15 | 7.3 | 31.1127 | YES | 3458
16 - 01 00 | 1.09 | 72 | 78.48 | 15 | 7.3 | 30.7603 | YES | 3408
17 - 01 58 | 1.17 | 74 | 86.58 | 15 | 7.4 | 32.213 | YES | 3300
18 - 14 05 | 1.1 | 75 | 82.5 | 15 | 7.4 | 31.9574 | YES | 3237
19 - 09 46 | 1.2 | 75 | 90 | 14 | 7.5 | 35.8488 | YES | 3244
20 - 18 06 | 1.04 | 75 | 78 | 14 | 7.4 | 33.9262 | YES | 3297
21 - 14 31 | 1.05 | 71 | 74.55 | 14 | 7.5 | 35.2434 | YES | 3456
22 - 18 22 | 1.02 | 69 | 70.38 | 14 | 7.5 | 35.1235 | YES | 3528
23 - 18 12 | 1.05 | 68 | 71.4 | 13 | 7.4 | 36.3007 | YES | 3606
24 - 05 03 | 0.89 | 68 | 60.52 | 12 | 7.2 | 35.8889 | YES | 3594
25 - 1516 | 0.89 | 69 | 61.41 | 9 | 7 | 40.6889 | YES | 3514
26 - 00 55 | 0.73 | 71 | 51.83 | 10 | 7.1 | 38.7693 | YES | 3506
27 - 23 15 | 0.94 | 69 | 64.86 | 10 | 7.1 | 39.6877 | YES | 3563
28 - 07 02 | 0.99 | 69 | 68.31 | 9 | 7.1 | 42.6115 | YES | 3536
29 - 17 15 | 0.86 | 69 | 59.34 | 10 | 7.3 | 42.1746 | YES | 3517
30 - 17 43 | 0.9 | 71 | 63.9 | 11 | 7.4 | 41.0865 | YES | 3497
31 -
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2