## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | JACKSON
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-11-24
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03
2 | 0.03 | 0.04 | 0.03 | 0.02 | 0.03 | 0.03 | 0.06
3 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
4 | 0.03 | 0.03 | 0.02 | 0.02 | 0.03 | 0.03 | 0.04
5 | 0.03 | 0.03 | 0.02 | 0.02 | 0.03 | 0.02 | 0.04
6 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03
7 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03 | 0.03
8 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
9 | 0.03 | 0.04 | 0.03 | 0.04 | 0.03 | 0.03 | 0.05
10 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
11 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.05
12 | 0.04 | 0.03 | 0.02 | 0.03 | 0.02 | 0.02 | 0.04
13 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.04
14 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
15 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
16 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
17 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.04
18 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
19 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.02 | 0.03
20 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03
21 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03 | 0.02 | 0.03
22 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03
23 | 0.03 | 0.02 | 0.03 | 0.02 | 0.03 | 0.03 | 0.04
24 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05
25 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.06
26 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
27 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
28 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
29 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
30 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03 | 0.06
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Alistair Andre
[5 empty] | SIGNATURE: |  |  | DATE:12-2-2024
[5 empty] | PHONE #: (541) - 488 - 5345 |  |  | CERT #: T-08640
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP : TP - | A
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 | Month/Year: | 2024-11-24 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 - 03 42 | 0.98 | 186 | 182.28 | 9 | 7.6 | 50.7921 | YES | 1325
2 - 05 49 | 1.04 | 177 | 184.08 | 9 | 7.6 | 51.1426 | YES | 1356
3 - 17 18 | 1.04 | 168 | 174.72 | 9 | 7.5 | 49.353 | YES | 1429
4 - 01 35 | 1 | 168 | 168 | 9 | 7.5 | 49.128 | YES | 1436
5 - 11 35 | 0.88 | 168 | 147.84 | 8 | 7.4 | 49.9937 | YES | 1450
6 - 19 14 | 0.87 | 168 | 146.16 | 8 | 7.4 | 49.9365 | YES | 1487
7 - 00 24 | 0.88 | 168 | 147.84 | 8 | 7.5 | 51.8086 | YES | 1490
8 - 17 39 | 0.91 | 177 | 161.07 | 8 | 7.4 | 50.1656 | YES | 1360
9 - 08 18 | 0.96 | 186 | 178.56 | 8 | 7.5 | 52.2867 | YES | 1351
10 - 13 07 | 0.99 | 186 | 184.14 | 8 | 7.5 | 52.4672 | YES | 1324
11 - 21 35 | 1.1 | 168 | 184.8 | 7 | 7.5 | 56.8379 | YES | 1454
12 - 0012 | 1.1 | 168 | 184.8 | 7 | 7.4 | 54.8311 | YES | 1439
13 - 04 24 | 0.92 | 177 | 162.84 | 8 | 7.4 | 50.223 | YES | 1391
14 - 22 48 | 1.11 | 177 | 196.47 | 8 | 7.6 | 55.1381 | YES | 1364
15 - 11 14 | 1.07 | 186 | 199 | 7 | 7.6 | 58.7197 | YES | 1333
16 - 22 03 | 0.99 | 177 | 175.23 | 8 | 7.5 | 52.4672 | YES | 1362
17 - 06 03 | 0.99 | 186 | 184.14 | 8 | 7.4 | 50.6271 | YES | 1333
18 - 01 39 | 0.9 | 177 | 159.3 | 8 | 7.3 | 48.3581 | YES | 1372
19 - 04 15 | 0.89 | 177 | 157.53 | 7 | 7.4 | 53.5203 | YES | 1358
20 - 06 28 | 1.01 | 161 | 162.61 | 7 | 7.4 | 54.2651 | YES | 1496
21 - 21 58 | 0.98 | 197 | 193.06 | 7 | 7.7 | 60.2471 | YES | 1256
22 - 16 40 | 1.06 | 177 | 187.62 | 7 | 7.4 | 54.5788 | YES | 1386
23 - 01 09 | 1.02 | 186 | 189.72 | 7 | 7.5 | 56.3146 | YES | 1346
24 - 01 27 | 0.92 | 197 | 181.24 | 7 | 7.4 | 53.7055 | YES | 1281
25 - 11 40 | 0.83 | 177 | 146.91 | 6 | 7.5 | 58.9435 | YES | 1355
26 - 03 03 | 0.85 | 177 | 150.45 | 6 | 7.4 | 56.9881 | YES | 1370
27 - 06 35 | 0.82 | 186 | 152.52 | 6 | 7.3 | 54.7856 | YES | 1351
28 - 05 52 | 0.83 | 186 | 154.38 | 5 | 7.3 | 58.6816 | YES | 1345
29 - 16 19 | 0.98 | 197 | 193.06 | 5 | 7.3 | 59.712 | YES | 1280
30 - 12 50 | 0.86 | 177 | 152.22 | 5 | 7.4 | 61.0538 | YES | 1366
31 -
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2