## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | JACKSON
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-12-01
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.03 | 0.03 | 0.04 | 0.05 | 0.03 | 0.03 | 0.05
2 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.05
3 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
4 | 0.03 | 0.05 | 0.04 | 0.03 | 0.03 | 0.04 | 0.06
5 | 0.03 | 0.03 | 0.04 | 0.03 | 0.04 | 0.05 | 0.05
6 | 0.04 | 0.04 | 0.03 | 0.04 | 0.03 | 0.04 | 0.05
7 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.06
8 | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.05
9 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03 | 0.04
10 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03
11 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
12 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
13 | 0.02 | 0.03 | 0.03 | 0.02 | 0.03 | 0.02 | 0.03
14 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
15 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.02 | 0.03
16 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
17 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
18 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.02 | 0.03
19 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.02 | 0.04
20 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
21 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
22 | 0.03 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03 | 0.03
23 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03 | 0.02 | 0.05
24 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03
25 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
26 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03
27 | 0.02 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03
28 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
29 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
30 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.04
31 | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.03 | 0.04
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Alistair Andre
[5 empty] | SIGNATURE: |  |  | DATE: 1/7/2025
[5 empty] | PHONE #: (541) - 488 - 5345 |  |  | CERT #: T-08640
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP : TP - | A
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 | Month/Year: |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 - 01 14 | 0.85 | 177 | 150.45 | 5 | 7.4 | 60.9828 | YES | 1393
2 - 13 07 | 0.95 | 168 | 159.6 | 4 | 7.5 | 68.4998 | YES | 1476
3 - 13 17 | 0.94 | 161 | 151.34 | 4 | 7.3 | 63.6155 | YES | 1500
4 - 09 15 | 0.95 | 161 | 152.95 | 4 | 7.2 | 61.4215 | YES | 1496
5 - 09 26 | 1.01 | 154 | 155.54 | 4 | 7.3 | 64.1373 | YES | 1604
6 - 03 33 | 0.88 | 177 | 155.76 | 4 | 7.3 | 63.1718 | YES | 1408
7 - 07 24 | 0.91 | 197 | 179.27 | 4 | 7.3 | 63.3932 | YES | 1276
8 - 07 49 | 0.87 | 186 | 161.82 | 5 | 7.3 | 58.9545 | YES | 1308
9 - 07 15 | 0.82 | 186 | 152.52 | 5 | 7.3 | 58.6136 | YES | 1305
10 - 03 33 | 0.83 | 197 | 163.51 | 5 | 7.3 | 58.6816 | YES | 1275
11 - 07 42 | 0.99 | 197 | 195.03 | 4 | 7.3 | 63.9877 | YES | 1272
12 - 18 39 | 1.01 | 197 | 198.97 | 4 | 7.3 | 64.1373 | YES | 1281
13 - 03 07 | 1 | 186 | 186 | 4 | 7.3 | 64.0625 | YES | 1296
14 - 14 49 | 1.03 | 197 | 202.91 | 4 | 7.3 | 64.2872 | YES | 1281
15 - 16 00 | 0.99 | 186 | 184.14 | 4 | 7.3 | 63.9877 | YES | 1286
16 - 19 05 | 0.9 | 197 | 177.3 | 4 | 7.3 | 63.3193 | YES | 1278
17 - 01 45 | 0.88 | 186 | 163.68 | 4 | 7.3 | 63.1718 | YES | 1303
18 - 12 44 | 0.87 | 197 | 171.39 | 4 | 7.3 | 63.0982 | YES | 1271
19 - 18 00 | 0.98 | 186 | 182.28 | 4 | 7.4 | 66.2802 | YES | 1317
20 - 01 45 | 1.05 | 197 | 206.85 | 4 | 7.4 | 66.8254 | YES | 1280
21 - 23 53 | 0.93 | 208 | 193.44 | 4 | 7.3 | 63.5413 | YES | 1197
22 - 01 07 | 0.92 | 197 | 181.24 | 4 | 7.3 | 63.4672 | YES | 1236
23 - 14 26 | 1.03 | 197 | 202.91 | 5 | 7.4 | 62.2741 | YES | 1232
24 - 01 01 | 0.94 | 197 | 185.18 | 5 | 7.4 | 61.6248 | YES | 1222
25 - 02 34 | 0.84 | 197 | 165.48 | 5 | 7.4 | 60.912 | YES | 1227
26 - 02 18 | 0.88 | 197 | 173.36 | 5 | 7.5 | 63.4554 | YES | 1218
27 - 02 01 | 0.77 | 197 | 151.69 | 5 | 7.3 | 58.2748 | YES | 1224
28 - 02 04 | 1.19 | 197 | 234.43 | 5 | 7.6 | 68.2368 | YES | 1219
29 - 16 52 | 0.94 | 197 | 185.18 | 6 | 7.6 | 61.9009 | YES | 1216
30 - 0412 | 0.93 | 197 | 183.21 | 6 | 7.6 | 61.8289 | YES | 1218
31 - 1323 | 0.83 | 197 | 163.51 | 6 | 7.7 | 63.3696 | YES | 1230
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2