## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | JACKSON
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-01-25
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03 | 0.04
2 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
3 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
4 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
5 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
6 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03
7 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
8 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.04
9 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
10 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.02 | 0.03
11 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03
12 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
13 | 0.02 | 0.02 | 0.03 | 0.04 | 0.03 | 0.03 | 0.04
14 | 0.02 | 0.03 | 0.02 | 0.04 | 0.03 | 0.02 | 0.06
15 | 0.03 | 0.02 | 0.03 | Plant Off Line | 0.03 | 0.02 | 0.06
16 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
17 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.02 | 0.03
18 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03
19 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
20 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
21 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
22 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
23 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
24 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
25 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
26 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
27 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
28 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.04
29 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03
30 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: 1/15 Plant off line for Tailrace maintanance from 0800 to 1300. No water flowed into the distribution system till Just after 1300. Highest NTU was 0.06 for the 24 hours. |  |  |  |  | PRINTED NAME: Alistair Andre
[5 empty] | SIGNATURE: |  |  | DATE:2/4/2025
[5 empty] | PHONE #: (541) - 488 - 5345 |  |  | CERT #: T-08640
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP : TP - | A
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 | Month/Year: |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 - 05 56 | 0.86 | 197 | 169.42 | 5 | 7.5 | 63.3075 | YES | 1280
2 - 21 06 | 0.77 | 186 | 143.4 | 6 | 7.5 | 58.5348 | YES | 1287
3 - 19 56 | 1.11 | 186 | 206.7 | 5 | 7.8 | 72.7264 | YES | 1292
4 -18 16 | 0.92 | 186 | 171.12 | 6 | 7.8 | 66.4106 | YES | 1299
5 -12 09 | 1.71 | 186 | 318 | 6 | 7.5 | 65.3046 | YES | 1293
6 - 15 06 | 1.95 | 177 | 345.15 | 6 | 7.5 | 67.1643 | YES | 1360
7 - 00 30 | 1.35 | 177 | 238.95 | 6 | 7.6 | 64.9332 | YES | 1367
8 - 04 45 | 1.11 | 186 | 206.7 | 6 | 7.6 | 63.1394 | YES | 1348
9 - 00 50 | 1.17 | 197 | 230 | 5 | 7.4 | 63.2986 | YES | 1273
10 - 10 41 | 1.05 | 197 | 206.85 | 5 | 7.5 | 64.7272 | YES | 1216
11 -07 17 | 1.32 | 197 | 260.04 | 5 | 7.5 | 66.8035 | YES | 1214
12 -11 06 | 1.12 | 208 | 232.96 | 5 | 7.5 | 65.2588 | YES | 1205
13 -14 06 | 0.94 | 161 | 151.34 | 4 | 7.5 | 68.4195 | YES | 1509
14 -06 19 | 0.89 | 168 | 149.52 | 5 | 7.5 | 63.5294 | YES | 1475
15 - 02 34 | 0.99 | 177 | 175.23 | 4 | 7.5 | 68.8219 | YES | 1417
16 - 13 51 | 1.04 | 186 | 193.44 | 4 | 7.3 | 64.3623 | YES | 1303
17 - 22 50 | 1.01 | 186 | 187.86 | 4 | 7.3 | 64.1373 | YES | 1289
18 - 01 06 | 1.05 | 197 | 206.85 | 4 | 7.3 | 64.4375 | YES | 1278
19- 22 09 | 1.35 | 197 | 265.95 | 3 | 7.4 | 74.1379 | YES | 1218
20 - 11 41 | 1.25 | 197 | 246.25 | 3 | 7.5 | 76.0078 | YES | 1220
21 - 16 07 | 1.23 | 186 | 228.78 | 3 | 7.5 | 75.8286 | YES | 1322
22 - 06 24 | 1.21 | 186 | 225.06 | 3 | 7.5 | 75.6499 | YES | 1295
23 - 06 03 | 1.22 | 197 | 240.34 | 3 | 7.6 | 78.5754 | YES | 1244
24 - 09 41 | 1.17 | 197 | 230.49 | 3 | 7.6 | 78.1123 | YES | 1220
25 -01 58 | 1.2 | 208 | 249.6 | 3 | 7.5 | 75.5607 | YES | 1213
26 - 18 08 | 1.18 | 208 | 245.44 | 3 | 7.5 | 75.3826 | YES | 1211
27 - 11 33 | 1.08 | 186 | 200.88 | 3 | 7.5 | 74.4988 | YES | 1293
28 - 04 22 | 1.06 | 197 | 208.82 | 3 | 7.6 | 77.1034 | YES | 1262
29 - 11 44 | 1.1 | 186 | 204.6 | 3 | 7.7 | 80.3735 | YES | 1333
30 - 04 30 | 1.14 | 186 | 212.04 | 3 | 7.8 | 83.7903 | YES | 1287
31 - 04 24 | 1.03 | 208 | 214.24 | 2 | 7.7 | 85.4257 | YES | 1210
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2