## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | JACKSON
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-02-01
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
2 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
3 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
4 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
5 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
6 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03
7 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
8 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
9 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03
10 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
11 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
12 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.02 | 0.03
13 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
14 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
15 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
16 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
17 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
18 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.04 | 0.04
19 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.07
20 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
21 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.04
22 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
23 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
24 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03
25 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.02 | 0.03
26 | 0.03 | 0.02 | 0.03 | 0.03 | 0.02 | 0.03 | 0.06
27 | 0.04 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.05
28 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
29
30
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Alistair Andre
[5 empty] | SIGNATURE: |  |  | DATE: 3/3/2025
[5 empty] | PHONE #: (541) - 488 - 5345 |  |  | CERT #: T-08640
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP : TP - | A
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 | Month/Year: |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 -20 31 | 1.06 | 197 | 208.82 | 3 | 7.7 | 79.9937 | YES | 1226
2 -04 45 | 1.1 | 208 | 228.8 | 3 | 7.6 | 77.4687 | YES | 1208
3 -14 37 | 1.19 | 208 | 247.52 | 3 | 7.5 | 75.4716 | YES | 1211
4 - 06 41 | 1.12 | 197 | 220.64 | 3 | 7.5 | 74.851 | YES | 1231
5 - 20 11 | 1.16 | 208 | 241.28 | 2 | 7.6 | 83.6075 | YES | 1170
6 - 17 25 | 1.17 | 197 | 230.49 | 2 | 7.7 | 86.859 | YES | 1238
7 - 14 39 | 1.14 | 197 | 224.58 | 2 | 7.7 | 86.5498 | YES | 1228
8 - 10 21 | 1.05 | 186 | 195.3 | 2 | 7.6 | 82.5236 | YES | 1212
9 - 15 10 | 1.19 | 186 | 221.34 | 2 | 7.6 | 83.9057 | YES | 1340
10 - 03 50 | 1.26 | 186 | 234.36 | 2 | 7.5 | 81.5396 | YES | 1349
11 - 03 06 | 1.19 | 177 | 210.63 | 2 | 7.6 | 83.9057 | YES | 1356
12 - 16 58 | 1.19 | 177 | 210.5 | 2 | 7.7 | 87.0658 | YES | 1368
13 - 03 26 | 1.11 | 186 | 206.7 | 2 | 7.7 | 86.2417 | YES | 1350
14 - 20 08 | 1.11 | 197 | 218.2 | 2 | 7.5 | 80.1037 | YES | 1279
15 - 14 10 | 1.19 | 197 | 234.43 | 2 | 7.5 | 80.8661 | YES | 1280
16 - 21 45 | 1.2 | 186 | 223.2 | 2 | 7.5 | 80.962 | YES | 1348
17 - 21 12 | 1.06 | 154 | 163.24 | 3 | 7.5 | 74.3234 | YES | 1575
18 - 20 11 | 1.13 | 161 | 181.93 | 3 | 7.6 | 77.7438 | YES | 1520
19 - 04 20 | 1.1 | 168 | 185.3 | 3 | 7.6 | 77.4687 | YES | 1493
20 - 22 55 | 1.11 | 186 | 206.7 | 3 | 7.8 | 83.4925 | YES | 1292
21 - 12 38 | 1.1 | 186 | 204.9 | 3 | 7.9 | 86.5333 | YES | 1292
22 - 00 44 | 1.06 | 197 | 208.82 | 3 | 7.5 | 74.3234 | YES | 1264
23 - 08 12 | 1.01 | 208 | 210.08 | 4 | 7.3 | 64.1373 | YES | 1196
24 - 19 25 | 1.01 | 197 | 198.97 | 4 | 7.2 | 61.852 | YES | 1221
25 - 10 28 | 1.01 | 208 | 210.08 | 4 | 7.2 | 61.852 | YES | 1207
26 - 17 16 | 0.98 | 177 | 173.4 | 4 | 7.1 | 59.4464 | YES | 1359
27 - 00 07 | 0.95 | 186 | 176.9 | 4 | 7.1 | 59.2397 | YES | 1349
28 - 17 42 | 0.98 | 186 | 182.5 | 5 | 7.3 | 59.712 | YES | 1297
29 -
30 -
31 -
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2