## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | JACKSON
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-03-01
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
2 | 0.03 | 0.03 | 0.04 | 0.02 | 0.02 | 0.03 | 0.04
3 | 0.03 | 0.04 | 0.05 | 0.03 | 0.03 | 0.03 | 0.06
4 | 0.03 | 0.04 | 0.02 | 0.02 | 0.02 | 0.02 | 0.05
5 | 0.03 | 0.04 | 0.03 | 0.02 | 0.02 | 0.02 | 0.06
6 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03
7 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
8 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
9 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03
10 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.04
11 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.03 | 0.03
12 | 0.03 | 0.02 | 0.03 | 0.02 | 0.03 | 0.03 | 0.04
13 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.04
14 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03 | 0.03 | 0.04
15 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
16 | 0.03 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.04
17 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
18 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05
19 | 0.04 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03 | 0.04
20 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
21 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
22 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
23 | 0.03 | 0.03 | 0.02 | 0.03 | 0.02 | 0.03 | 0.04
24 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
25 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.05
26 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.05
27 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
28 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.02 | 0.04
29 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03
30 | 0.03 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03
31 | 0.02 | 0.03 | 0.03 | 0.03 | 0.02 | 0.03 | 0.04
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Alistair Andre
[5 empty] | SIGNATURE: |  |  | DATE: 4/1/2025
[5 empty] | PHONE #: (541) - 488 - 5345 |  |  | CERT #: T-08640
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP : TP - | A
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 | Month/Year: |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1- 15 11 | 1.19 | 186 | 221.34 | 4 | 7.4 | 67.9304 | YES | 1347
2- 02 53 | 1.15 | 177 | 203.55 | 5 | 7.2 | 58.7415 | YES | 1371
3 -00 32 | 1.28 | 186 | 238.08 | 4 | 7.2 | 63.8296 | YES | 1353
4 - 08 02 | 1.11 | 177 | 196.4 | 5 | 7.2 | 58.4697 | YES | 1380
5 - 10 53 | 1.15 | 186 | 214.2 | 5 | 7.2 | 58.7415 | YES | 1348
6 - 06 29 | 1.03 | 197 | 202.5 | 5 | 7.2 | 57.9301 | YES | 1272
7 - 09 57 | 1 | 197 | 196.6 | 5 | 7.2 | 57.7291 | YES | 1224
8 - 16 41 | 1.44 | 197 | 283.68 | 5 | 7.3 | 62.9953 | YES | 1225
9 - 06 44 | 1.33 | 197 | 262.01 | 5 | 7.2 | 59.9817 | YES | 1224
10 - 22 32 | 1.01 | 177 | 178.77 | 5 | 7.2 | 57.796 | YES | 1361
11 - 15 45 | 0.96 | 177 | 169.8 | 5 | 7.2 | 57.4623 | YES | 1365
12 - 09 18 | 0.92 | 177 | 162.84 | 5 | 7.2 | 57.1968 | YES | 1357
13 - 05 47 | 0.97 | 177 | 171.6 | 5 | 7.3 | 59.6427 | YES | 1357
14 - 01 24 | 1.19 | 197 | 233.9 | 5 | 7.2 | 59.0147 | YES | 1282
15 - 00 22 | 1.18 | 197 | 232.46 | 5 | 7.3 | 61.1164 | YES | 1235
16 - 20 27 | 1.37 | 197 | 269.89 | 5 | 7.2 | 60.2611 | YES | 1229
17 - 04 01 | 1.34 | 197 | 263.98 | 5 | 7.2 | 60.0515 | YES | 1218
18 - 15 42 | 1.12 | 197 | 220.2 | 5 | 7.3 | 60.6914 | YES | 1244
19 - 22 42 | 1.08 | 186 | 201.1 | 5 | 7.1 | 56.2053 | YES | 1294
20 - 12 16 | 0.96 | 177 | 169.8 | 5 | 7.2 | 57.4623 | YES | 1355
21 - 02 18 | 1.06 | 177 | 187.5 | 5 | 7.2 | 58.1318 | YES | 1368
22 - 04 37 | 1.29 | 177 | 228.33 | 5 | 7.3 | 61.9038 | YES | 1366
23 - 10 20 | 1.06 | 186 | 197.16 | 5 | 7.3 | 60.2695 | YES | 1302
24 - 02 52 | 1.04 | 186 | 193.44 | 5 | 7.3 | 60.1296 | YES | 1290
25 - 09 07 | 1.1 | 186 | 204.9 | 5 | 7.2 | 58.4019 | YES | 1292
26 - 14 05 | 1.09 | 186 | 203 | 6 | 7.4 | 58.5945 | YES | 1285
27 - 16 18 | 1.09 | 177 | 192.8 | 6 | 7.6 | 62.9923 | YES | 1368
28 - 0743 | 1.14 | 177 | 201.7 | 6 | 7.6 | 63.3607 | YES | 1357
29 - 0115 | 1.13 | 177 | 200.01 | 7 | 7.5 | 57.0356 | YES | 1367
30 - 0416 | 1.28 | 208 | 266.24 | 7 | 7.5 | 58.0349 | YES | 1201
31 - 0050 | 1.15 | 208 | 239.2 | 7 | 7.4 | 55.1483 | YES | 1208
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2