## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | JACKSON
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-04-01
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02 | 0.03
2 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
3 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
4 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
5 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
6 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
7 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
8 | 0.02 | 0.03 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03
9 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
10 | 0.03 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
11 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
12 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
13 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
14 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03 | 0.03 | 0.06
15 | 0.02 | 0.05 | 0.02 | 0.02 | 0.02 | 0.03 | 0.06
16 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
17 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
18 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03 | 0.02 | 0.05
19 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
20 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03
21 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
22 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
23 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03
24 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.04 | 0.06
25 | 0.03 | 0.02 | 0.03 | 0.04 | 0.02 | 0.02 | 0.04
26 | 0.03 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03 | 0.03
27 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
28 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
29 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
30 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.06
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Alistair Andre
[5 empty] | SIGNATURE: |  |  | DATE:5/1/2025
[5 empty] | PHONE #: (541) - 488 - 5345 |  |  | CERT #: T-08640
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP : TP - | A
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 | Month/Year: | 2025-04-01 | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 - 01 08 | 1.12 | 197 | 220.64 | 6 | 7.4 | 58.7988 | YES | 1259
2 - 08 51 | 1.08 | 177 | 191.1 | 6 | 7.4 | 58.5266 | YES | 1395
3 - 06 09 | 1.06 | 186 | 197.4 | 6 | 7.5 | 60.5391 | YES | 1319
4 - 15 37 | 1.12 | 186 | 208.6 | 6 | 7.6 | 63.2131 | YES | 1299
5 - 04 36 | 1.04 | 186 | 193.44 | 6 | 7.4 | 58.2559 | YES | 1294
6 - 14 24 | 1.29 | 186 | 239.94 | 6 | 7.5 | 62.1813 | YES | 1331
7 - 15 52 | 1.1 | 186 | 204.6 | 6 | 7.6 | 63.0658 | YES | 1343
8 - 01 26 | 0.96 | 186 | 178.56 | 6 | 7.5 | 59.8398 | YES | 1349
9 - 06 30 | 0.99 | 186 | 184.4 | 7 | 7.4 | 54.1402 | YES | 1352
10 - 17 53 | 1.04 | 161 | 167.3 | 7 | 7.3 | 52.5372 | YES | 1561
11 - 00 12 | 1.09 | 161 | 175.3 | 7 | 7.3 | 52.84 | YES | 1554
12 - 00 40 | 1.01 | 161 | 162.61 | 7 | 7.3 | 52.3564 | YES | 1509
13 - 06 44 | 1.26 | 168 | 211.68 | 7 | 7.3 | 53.8839 | YES | 1469
14 - 15 13 | 1.15 | 147 | 169.05 | 8 | 7.3 | 49.7586 | YES | 1664
15 - 20 52 | 1.19 | 147 | 174.93 | 7 | 7.3 | 53.4514 | YES | 1686
16 - 23 12 | 1.13 | 142 | 159.9 | 8 | 7.3 | 49.645 | YES | 1755
17 - 13 44 | 1.13 | 122 | 137.86 | 8 | 7.4 | 51.4461 | YES | 1985
18 - 17 59 | 1.13 | 122 | 137.86 | 8 | 7.3 | 49.645 | YES | 2018
19 - 12 12 | 1.24 | 126 | 156.24 | 8 | 7.3 | 50.2736 | YES | 1979
20 - 16 00 | 1.13 | 122 | 137.86 | 8 | 7.3 | 49.645 | YES | 2008
21 - 04 09 | 1.16 | 126 | 146.16 | 9 | 7.3 | 46.6069 | YES | 1937
22 - 13 27 | 1.26 | 114 | 143.64 | 8 | 7.4 | 52.2195 | YES | 2137
23 - 18 17 | 1.38 | 111 | 152.6 | 8 | 7.4 | 52.9446 | YES | 2211
24 - 11 14 | 1.27 | 114 | 145 | 8 | 7.4 | 52.2795 | YES | 2178
25 - 20 08 | 1.12 | 111 | 123.8 | 8 | 7.4 | 51.3871 | YES | 2215
26 - 06 26 | 1.08 | 114 | 123.12 | 8 | 7.4 | 51.152 | YES | 2161
27 - 00 44 | 1.05 | 122 | 128.1 | 8 | 7.4 | 50.9764 | YES | 1981
28 - 19 02 | 1.25 | 142 | 177.5 | 8 | 7.4 | 52.1595 | YES | 1766
29 - 12 26 | 1.13 | 142 | 160.46 | 8 | 7.4 | 51.4461 | YES | 1744
30 - 16 00 | 1.2 | 137 | 164.4 | 8 | 7.4 | 51.861 | YES | 2178
31 -
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2