## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | JACKSON
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-05-01
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.06
2 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
3 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
4 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
5 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03
6 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
7 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
8 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
9 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
10 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
11 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
12 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
13 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
14 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
15 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
16 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03
17 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
18 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
19 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
20 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
21 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
22 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
23 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
24 | 0.02 | 0.02 | 0.03 | 0.03 | 0.02 | 0.02 | 0.03
25 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
26 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
27 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
28 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
29 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
30 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
31 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Alistair Andre
[5 empty] | SIGNATURE: |  |  | DATE: 6/3/2025
[5 empty] | PHONE #: (541) - 488 - 5345 |  |  | CERT #: T-08640
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP : TP - | A
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 | Month/Year: |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 - 10 21 | 1.25 | 101 | 126.25 | 8 | 7.4 | 52.1595 | YES | 2396
2 - 03 23 | 1.08 | 108 | 116.64 | 9 | 7.4 | 47.8493 | YES | 2415
3 -02 43 | 1.07 | 186 | 199.02 | 9 | 7.4 | 47.7948 | YES | 1354
4 - 08 44 | 1.18 | 197 | 232.46 | 9 | 7.4 | 48.3978 | YES | 1216
5 - 02 21 | 1.2 | 186 | 223.2 | 9 | 7.4 | 48.5084 | YES | 1321
6 - 22 30 | 1.12 | 186 | 208.6 | 8 | 7.4 | 51.3871 | YES | 1352
7 - 12 53 | 1.14 | 154 | 175.4 | 9 | 7.4 | 48.1776 | YES | 1575
8 - 03 33 | 1.14 | 161 | 183.4 | 9 | 7.4 | 48.1776 | YES | 1547
9 - 10 58 | 1.18 | 168 | 198.8 | 9 | 7.4 | 48.3978 | YES | 1426
10 - 00 57 | 1.21 | 177 | 214.17 | 9 | 7.4 | 48.5637 | YES | 1415
11 - 20 56 | 1.23 | 186 | 228.78 | 9 | 7.4 | 48.6747 | YES | 1292
12 - 06 53 | 1.16 | 186 | 215.76 | 9 | 7.4 | 48.2876 | YES | 1295
13 - 11 56 | 1.05 | 221 | 232.2 | 10 | 7.4 | 44.6273 | YES | 1103
14 - 14 05 | 1.06 | 208 | 220.6 | 10 | 7.4 | 44.6779 | YES | 1168
15 - 03 14 | 1.03 | 236 | 243 | 10 | 7.4 | 44.5265 | YES | 1039
16 - 15 40 | 1.13 | 236 | 266.6 | 10 | 7.4 | 45.0333 | YES | 1028
17 - 05 04 | 1.19 | 221 | 262.99 | 9 | 7.4 | 48.4531 | YES | 1081
18 - 22 42 | 1.2 | 186 | 223.2 | 9 | 7.4 | 48.5084 | YES | 1305
19 - 08 43 | 1.21 | 208 | 251.68 | 9 | 7.4 | 48.5637 | YES | 1170
20 - 18 39 | 1.12 | 114 | 127.8 | 9 | 7.4 | 48.0679 | YES | 2124
21 - 23 10 | 1.08 | 88 | 95.5 | 9 | 7.4 | 47.8493 | YES | 2746
22 - 09 57 | 1.24 | 86 | 107 | 9 | 7.4 | 48.7303 | YES | 2841
23 - 03 41 | 1.09 | 88 | 96.4 | 10 | 7.4 | 44.8298 | YES | 2771
24 - 03 34 | 1.17 | 93 | 108.81 | 9 | 7.4 | 48.3427 | YES | 2668
25 - 20 05 | 1.1 | 91 | 100.1 | 10 | 7.4 | 44.8806 | YES | 2682
26 - 17 27 | 1.07 | 86 | 92.02 | 10 | 7.4 | 44.7284 | YES | 2842
27 - 20 41 | 1.06 | 77 | 81.62 | 10 | 7.4 | 44.6779 | YES | 3223
28 - 02 22 | 1.06 | 77 | 81.5 | 10 | 7.4 | 44.6779 | YES | 3215
29 - 13 08 | 1.13 | 75 | 85.1 | 10 | 7.4 | 45.0333 | YES | 3234
30 - 13 43 | 1.01 | 74 | 74.5 | 10 | 7.4 | 44.4259 | YES | 3317
31 - 01 18 | 0.98 | 75 | 73.5 | 11 | 7.4 | 41.4569 | YES | 3265
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2