## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | JACKSON
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-06-01
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
2 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
3 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
4 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03
5 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
6 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
7 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
8 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.02 | 0.03
9 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
10 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
11 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
12 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
13 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
14 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
15 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
16 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
17 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
18 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
19 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
20 | 0.02 | 0.02 | 0.021 | 0.02 | 0.02 | 0.02 | 0.03
21 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
22 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03
23 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
24 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
25 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
26 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
27 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
28 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
29 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
30 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Alistair Andre
[5 empty] | SIGNATURE: |  |  | DATE: 7/2/2025
[5 empty] | PHONE #: (541) - 488 - 5345 |  |  | CERT #: T-08640
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP : TP - | A
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 | Month/Year: |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 - 10 03 | 1.13 | 79 | 89.27 | 10 | 7.4 | 45.0333 | YES | 3154
2 -10 15 | 1.04 | 77 | 80.08 | 10 | 7.4 | 44.5769 | YES | 3189
3 - 00 35 | 1.07 | 77 | 82.3 | 11 | 7.4 | 41.8779 | YES | 3180
4 - 11 09 | 1.07 | 72 | 77.3 | 10 | 7.4 | 44.7284 | YES | 3431
5 - 10 04 | 1.07 | 72 | 77.3 | 11 | 7.4 | 41.8779 | YES | 3403
6 - 00 48 | 1.08 | 74 | 79.6 | 11 | 7.4 | 41.925 | YES | 3333
7 - 21 24 | 1.01 | 69 | 69.69 | 12 | 7.4 | 38.9667 | YES | 3526
8 - 05 39 | 1.12 | 67 | 75.04 | 12 | 7.4 | 39.4475 | YES | 3663
9 - 13 56 | 1.06 | 67 | 71.02 | 12 | 7.4 | 39.1844 | YES | 3682
10 - 06 10 | 1.15 | 67 | 76.8 | 12 | 7.4 | 39.5798 | YES | 3660
11 - 03 30 | 1.04 | 68 | 70.8 | 12 | 7.4 | 39.0972 | YES | 3580
12 - 08 18 | 1.1 | 71 | 77.8 | 12 | 7.4 | 39.3596 | YES | 3503
13 - 06 20 | 1.13 | 71 | 80 | 12 | 7.4 | 39.4915 | YES | 3470
14 - 00 40 | 1.04 | 72 | 74.88 | 12 | 7.4 | 39.0972 | YES | 3429
15 - 19 15 | 1.01 | 72 | 72.72 | 12 | 7.4 | 38.9667 | YES | 3364
16 - 22 11 | 1.04 | 71 | 73.84 | 12 | 7.4 | 39.0972 | YES | 3458
17 - 15 07 | 1.06 | 69 | 73.5 | 13 | 7.4 | 36.3419 | YES | 3538
18 - 19 27 | 1.08 | 69 | 74.52 | 13 | 7.4 | 36.4245 | YES | 3522
19 - 07 59 | 1.11 | 69 | 77 | 12 | 7.4 | 39.4035 | YES | 3527
20 - 02 43 | 1.04 | 72 | 75.1 | 13 | 7.4 | 36.2595 | YES | 3432
21 - 00 27 | 1 | 80 | 80 | 13 | 7.4 | 36.0953 | YES | 3028
22 - 14 58 | 1.03 | 82 | 84.46 | 12 | 7.4 | 39.0536 | YES | 2977
23 - 17 47 | 0.97 | 72 | 69.84 | 12 | 7.4 | 38.7935 | YES | 3432
24 - 07 18 | 1.11 | 71 | 78.6 | 11 | 7.4 | 42.0666 | YES | 3473
25 - 15 45 | 1.02 | 68 | 69.36 | 13 | 7.4 | 36.1773 | YES | 3606
26 - 09 58 | 1.08 | 68 | 73.5 | 12 | 7.4 | 39.2719 | YES | 3601
27 - 19 10 | 1.05 | 71 | 74.3 | 12 | 7.4 | 39.1408 | YES | 3457
28 - 21 10 | 1.13 | 68 | 76.9 | 13 | 7.4 | 36.6318 | YES | 3623
29 - 04 58 | 1.01 | 69 | 69.69 | 13 | 7.4 | 36.1363 | YES | 3562
30 - 11 58 | 1 | 66 | 66 | 13 | 7.4 | 36.0953 | YES | 3755
31 -
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2