## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | JACKSON
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-07-01
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.04
2 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
3 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
4 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
5 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
6 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
7 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
8 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
9 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
10 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
11 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
12 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
13 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
14 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
15 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
16 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
17 | 0.03 | 0.03 | 0.02 | 0.02 | 0.03 | 0.02 | 0.03
18 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
19 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
20 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.03
21 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
22 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
23 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
24 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
25 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
26 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
27 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
28 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
29 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
30 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
31 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes | Yes |  | Yes
All turbidity readings < IFE2 triggers |  |  |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Alistair Andre
[5 empty] | SIGNATURE: |  |  | DATE: 8/4/2025
[5 empty] | PHONE #: (541) - 488 - 5345 |  |  | CERT #: T-08640
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP : TP - | A
System Name: | ASHLAND WATER DEPARTMENT |  |  | ID#: 4100047 | Month/Year: |  | Disinfection Giardia Log Inactive: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 - 18 52 | 1.05 | 66 | 68.8 | 13 | 7.4 | 36.3007 | YES | 3768
2 - 22 51 | 1.09 | 62 | 67.7 | 13 | 7.3 | 35.144 | YES | 3992
3 - 03 24 | 1.1 | 62 | 68.3 | 13 | 7.4 | 36.5073 | YES | 3976
4 - 02 05 | 1.04 | 67 | 69.4 | 14 | 7.4 | 33.9262 | YES | 3680
5 - 1801 | 1.06 | 74 | 78.1 | 14 | 7.4 | 34.0035 | YES | 3334
6 - 1220 | 1.1 | 67 | 73.4 | 14 | 7.4 | 34.1584 | YES | 3669
7 - 1356 | 1.03 | 64 | 66.3 | 14 | 7.4 | 33.8877 | YES | 3820
8 - 0306 | 1.07 | 64 | 68.48 | 14 | 7.4 | 34.0421 | YES | 3798
9 - 2049 | 1.13 | 56 | 63.28 | 14 | 7.4 | 34.2751 | YES | 4367
10 - 0740 | 1.21 | 56 | 68 | 14 | 7.4 | 34.5881 | YES | 4373
11 - 1218 | 1.02 | 61 | 62.22 | 14 | 7.4 | 33.8492 | YES | 4045
12 - 0041 | 1.06 | 60 | 63.6 | 15 | 7.4 | 31.8122 | YES | 4127
13 - 0939 | 0.98 | 64 | 62.72 | 15 | 7.3 | 30.3771 | YES | 3851
14 - 1618 | 0.87 | 62 | 53.94 | 15 | 7.3 | 29.9985 | YES | 3944
15 - 2003 | 0.72 | 60 | 43.2 | 15 | 7.3 | 29.4897 | YES | 4098
16 - 1859 | 1.12 | 57 | 63.9 | 16 | 7.3 | 28.8718 | YES | 4281
17 - 0141 | 1 | 57 | 57.1 | 15 | 7.3 | 30.4464 | YES | 4279
18 - 1328 | 1 | 60 | 60 | 16 | 7.3 | 28.4789 | YES | 4065
19 - 0148 | 1.1 | 61 | 67.1 | 16 | 7.3 | 28.8059 | YES | 4052
20 - 1844 | 0.96 | 61 | 58.56 | 16 | 7.3 | 28.3492 | YES | 4000
21 - 0838 | 0.96 | 61 | 58.56 | 16 | 7.3 | 28.3492 | YES | 4040
22 - 1201 | 1.02 | 63 | 64.26 | 16 | 7.3 | 28.5441 | YES | 3884
23 - 1344 | 0.93 | 61 | 56.73 | 16 | 7.3 | 28.2522 | YES | 4015
24 - 1715 | 1.1 | 61 | 67.1 | 16 | 7.3 | 28.8059 | YES | 4016
25 - 1721 | 1.1 | 59 | 64.9 | 16 | 7.3 | 28.8059 | YES | 4156
26 - 0146 | 1.1 | 59 | 64.9 | 16 | 7.3 | 28.8059 | YES | 4141
27 - 1943 | 1.06 | 63 | 66.78 | 17 | 7.3 | 26.8188 | YES | 3916
28 - 1412 | 1.05 | 63 | 66.15 | 17 | 7.3 | 26.7881 | YES | 3923
29 - 2013 | 0.98 | 61 | 59.78 | 17 | 7.3 | 26.5745 | YES | 3994
30 - 1843 | 1 | 59 | 59 | 17 | 7.3 | 26.6353 | YES | 4142
31 - 0512 | 1.09 | 59 | 64.4 | 17 | 7.3 | 26.9109 | YES | 4155
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2