## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | CLATSOP
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-12-24
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.16 |  |  |  | 0.16
2 |  |  | 0.11 |  |  |  | 0.11
3 |  |  | 0.18 |  |  |  | 0.18
4 |  |  | 0.22 |  |  |  | 0.22
5 |  |  | 0.19 |  |  |  | 0.19
6 |  |  | 0.26 |  |  |  | 0.26
7 |  |  | 0.13 |  |  |  | 0.13
8 |  |  | 0.24 |  |  |  | 0.24
9 |  |  | 0.35 |  |  |  | 0.35
10 |  |  | 0.23 |  |  |  | 0.23
11 |  |  | 0.15 |  |  |  | 0.15
12 |  |  | 0.14 |  |  |  | 0.14
13 |  |  | 0.26 |  |  |  | 0.26
14 |  |  | 0.15 |  |  |  | 0.15
15 |  |  | 0.11 |  |  |  | 0.11
16 |  |  | 0.14 |  |  |  | 0.14
17 |  |  | 0.2 |  |  |  | 0.2
18 |  |  | 0.29 |  |  |  | 0.29
19 |  |  | 0.43 |  |  |  | 0.43
20 |  |  | 0.38 |  |  |  | 0.38
21 |  |  | 0.28 |  |  |  | 0.28
22 |  |  | 0.22 |  |  |  | 0.22
23 |  |  | 0.42 |  |  |  | 0.42
24 |  |  | 0.31 |  |  |  | 0.31
25 |  |  | 0.44 |  |  |  | 0.44
26 |  |  | 0.44 |  |  |  | 0.44
27 |  |  | 0.34 |  |  |  | 0.34
28 |  |  | 0.39 |  |  |  | 0.39
29 |  |  | 0.31 |  |  |  | 0.31
30 |  |  | 0.35 |  |  |  | 0.352
31 |  |  | 0.23 |  |  |  | 0.23
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Eric Bufkin
[5 empty] | SIGNATURE: |  |  | DATE: 01/09/2025
[5 empty] | PHONE #: ( 503 ) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-12-24 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.06 | 149 | 157.94 | 9.6 | 8.65 | 71.9501 | YES | 103
2 | 1.26 | 149 | 187.74 | 8.2 | 8.74 | 83.8746 | YES | 91
3 | 1.65 | 149 | 245.85 | 6 | 7.84 | 73.4189 | YES | 112
4 | 1.92 | 149 | 286.08 | 6.1 | 7.74 | 72.5629 | YES | 94
5 | 1.74 | 149 | 259.26 | 6.9 | 7.73 | 67.0085 | YES | 106
6 | 1.43 | 149 | 213.07 | 7.5 | 7.61 | 59.3989 | YES | 106
7 | 1.47 | 149 | 219.03 | 8.2 | 7.8 | 60.9545 | YES | 97
8 | 1.63 | 149 | 242.87 | 7 | 8.12 | 75.77 | YES | 79
9 | 0.73 | 149 | 108.77 | 7 | 7.96 | 64.3016 | YES | 85
10 | 0.68 | 149 | 101.32 | 6.6 | 7.56 | 56.84 | YES | 93
11 | 0.75 | 149 | 111.75 | 6.6 | 7.88 | 64.3365 | YES | 96
12 | 1.05 | 149 | 156.45 | 6.8 | 7.83 | 64.5442 | YES | 117
13 | 1.1 | 149 | 163.9 | 8.5 | 8.61 | 76.8409 | YES | 74
14 | 1.22 | 149 | 181.78 | 7.7 | 7.52 | 55.3692 | YES | 96
15 | 1.24 | 149 | 184.76 | 7.8 | 7.56 | 55.9224 | YES | 120
16 | 1.14 | 149 | 169.86 | 7 | 7.65 | 60.278 | YES | 96
17 | 1.61 | 149 | 239.89 | 8.5 | 7.39 | 52.381 | YES | 95
18 | 1.13 | 149 | 168.37 | 7.9 | 8.04 | 65.235 | YES | 98
19 | 1.71 | 149 | 254.79 | 8.2 | 7.68 | 60.0163 | YES | 94
20 | 1.47 | 149 | 219.03 | 8.9 | 7.48 | 51.8215 | YES | 96
21 | 1.03 | 149 | 153.47 | 9.1 | 8.16 | 62.0621 | YES | 112
22 | 1.12 | 149 | 166.88 | 9.1 | 8.56 | 72.5615 | YES | 105
23 | 1.4 | 149 | 208.6 | 8.5 | 8.41 | 73.9731 | YES | 115
24 | 1.15 | 149 | 171.35 | 8.8 | 8.07 | 62.1714 | YES | 113
25 | 1.45 | 149 | 216.05 | 8.6 | 8.04 | 64.5617 | YES | 111
26 | 1.45 | 149 | 216.05 | 8.6 | 7.98 | 63.17 | YES | 114
27 | 0.97 | 149 | 144.53 | 8.4 | 7.98 | 60.5543 | YES | 107
28 | 0.74 | 149 | 110.26 | 9 | 7.38 | 45.7107 | YES | 104
29 | 0.44 | 149 | 65.56 | 9 | 8.16 | 58.3445 | YES | 117
30 | 0.57 | 149 | 84.93 | 8.4 | 8.26 | 63.9722 | YES | 85
31 | 0.69 | 149 | 102.81 | 8.2 | 8.14 | 62.9606 | YES | 104
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2