## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | CLATSOP
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-01-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.29 |  |  |  | 0.29
2 |  |  | 0.17 |  |  |  | 0.17
3 |  |  | 0.28 |  |  |  | 0.28
4 |  |  | 0.65 |  |  |  | 0.65
5 |  |  | 0.32 |  |  |  | 0.32
6 |  |  | 0.26 |  |  |  | 0.26
7 |  |  | 0.28 |  |  |  | 0.28
8 |  |  | 0.45 |  |  |  | 0.45
9 |  |  | 0.16 |  |  |  | 0.16
10 |  |  | 0.19 |  |  |  | 0.19
11 |  |  | 0.26 |  |  |  | 0.26
12 |  |  | 0.34 |  |  |  | 0.34
13 |  |  | 0.27 |  |  |  | 0.274
14 |  |  | 0.25 |  |  |  | 0.25
15 |  |  | 0.32 |  |  |  | 0.32
16 |  |  | 0.38 |  |  |  | 0.38
17 |  |  | 0.19 |  |  |  | 0.19
18 |  |  | 0.69 |  |  |  | 0.69
19 |  |  | 0.44 |  |  |  | 0.44
20 |  |  | 0.36 |  |  |  | 0.36
21 |  |  | 0.08 |  |  |  | 0.08
22 |  |  | 0.27 |  |  |  | 0.27
23 |  |  | 0.11 |  |  |  | 0.11
24 |  |  | 0.27 |  |  |  | 0.27
25 |  |  | 0.38 |  |  |  | 0.38
26 |  |  | 0.14 |  |  |  | 0.14
27 |  |  | 0.13 |  |  |  | 0.13
28 |  |  | 0.3 |  |  |  | 0.3
29 |  |  | 0.16 |  |  |  | 0.16
30 |  |  | 0.18 |  |  |  | 0.18
31 |  |  | 0.18 |  |  |  | 0.18
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE: 02/09/2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-01-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.02 | 149 | 151.98 | 7.8 | 8.06 | 65.3162 | YES | 97
2 | 0.98 | 149 | 146.02 | 8.4 | 7.88 | 58.4735 | YES | 102
3 | 0.96 | 149 | 143.04 | 8.7 | 7.81 | 55.7443 | YES
4 | 1.1 | 149 | 163.9 | 8.1 | 7.62 | 55.0989 | YES
5 | 1.1 | 149 | 163.9 | 9.6 | 7.78 | 52.7512 | YES
6 | 1.2 | 149 | 178.8 | 8.2 | 8 | 63.5087 | YES
7 | 0.98 | 149 | 146.02 | 7.9 | 7.65 | 55.6754 | YES
8 | 0.93 | 149 | 138.57 | 8 | 7.64 | 54.7861 | YES
9 | 0.76 | 149 | 113.24 | 7.7 | 7.72 | 56.4178 | YES
10 | 0.79 | 149 | 117.71 | 8 | 7.62 | 53.5243 | YES
11 | 1.79 | 149 | 266.71 | 8.1 | 7.17 | 50.7772 | YES
12 | 1.37 | 149 | 204.13 | 8.1 | 7.53 | 55.0349 | YES
13 | 0.74 | 149 | 110.26 | 7.3 | 7.47 | 52.8634 | YES
14 | 1.23 | 149 | 183.27 | 6.4 | 7.63 | 62.9906 | YES
15 | 1.58 | 149 | 235.42 | 6.1 | 7.59 | 66.0084 | YES
16 | 1.3 | 149 | 193.7 | 6.5 | 7.48 | 59.7409 | YES
17 | 1.43 | 149 | 213.07 | 6 | 7.38 | 60.5149 | YES
18 | 1.33 | 149 | 198.17 | 6.2 | 7.33 | 57.9553 | YES
19 | 1.64 | 149 | 244.36 | 5.8 | 7.67 | 69.8622 | YES
20 | 1.98 | 149 | 295.02 | 5.1 | 7.59 | 74.0932 | YES
21 | 1.12 | 149 | 166.88 | 5.9 | 8.06 | 75.2859 | YES
22 | 1.28 | 149 | 190.72 | 4.4 | 8.37 | 95.4735 | YES
23 | 0.96 | 149 | 143.04 | 4.2 | 8.46 | 96.3545 | YES
24 | 1.46 | 149 | 217.54 | 4.2 | 8.39 | 99.6614 | YES
25 | 2 | 149 | 298 | 4.4 | 8.32 | 102.1426 | YES
26 | 1.26 | 149 | 187.74 | 5 | 8.51 | 96.221 | YES
27 | 1.36 | 149 | 202.64 | 4 | 8.44 | 101.7401 | YES
28 | 1.66 | 149 | 247.34 | 3.5 | 8.39 | 107.2066 | YES
29 | 2.1 | 149 | 312.9 | 3.9 | 8.51 | 114.9469 | YES
30 | 1.85 | 149 | 275.65 | 4.7 | 8.27 | 96.4319 | YES
31 | 1.64 | 149 | 244.36 | 6.2 | 8.31 | 85.9911 | YES
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2