## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | CLATSOP
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-02-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.16 |  |  |  | 0.16
2 |  |  | 0.16 |  |  |  | 0.16
3 |  |  | 0.18 |  |  |  | 0.18
4 |  |  | 0.19 |  |  |  | 0.19
5 |  |  | 0.17 |  |  |  | 0.17
6 |  |  | 0.19 |  |  |  | 0.19
7 |  |  | 0.15 |  |  |  | 0.15
8 |  |  | 0.16 |  |  |  | 0.16
9 |  |  | 0.17 |  |  |  | 0.17
10 |  |  | 0.16 |  |  |  | 0.16
11 |  |  | 0.2 |  |  |  | 0.2
12 |  |  | 0.14 |  |  |  | 0.14
13 |  |  | 0.16 |  |  |  | 0.16
14 |  |  | 0.16 |  |  |  | 0.16
15 |  |  | 0.11 |  |  |  | 0.11
16 |  |  | 0.19 |  |  |  | 0.19
17 |  |  | 0.11 |  |  |  | 0.11
18 |  |  | 0.32 |  |  |  | 0.32
19 |  |  | 0.11 |  |  |  | 0.11
20 |  |  | off |  |  |  | off
21 |  |  | 0.44 |  |  |  | 0.44
22 |  |  | 0.44 |  |  |  | 0.44
23 |  |  | 0.31 |  |  |  | 0.31
24 |  |  | 0.26 |  |  |  | 0.26
25 |  |  | 0.27 |  |  |  | 0.27
26 |  |  | 0.58 |  |  |  | 0.58
27 |  |  | 0.12 |  |  |  | 0.12
28 |  |  | 0.23 |  |  |  | 0.23
29
30
31
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE: 03/07/2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-02-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.64 | 149 | 244.36 | 5 | 8.35 | 94.8751 | YES
2 | 1.31 | 149 | 195.19 | 3.9 | 8.1 | 89.7506 | YES
3 | 0.99 | 149 | 147.51 | 5.8 | 8.07 | 74.9273 | YES
4 | 1.34 | 149 | 199.66 | 4.1 | 8.13 | 89.8208 | YES
5 | 1.51 | 149 | 224.99 | 3.7 | 8.14 | 94.6 | YES
6 | 1.36 | 149 | 202.64 | 3.9 | 8.22 | 94.3987 | YES
7 | 1.39 | 149 | 207.11 | 3.7 | 8.15 | 93.6017 | YES
8 | 1.6 | 149 | 238.4 | 4 | 8.24 | 97.1891 | YES
9 | 1.67 | 149 | 248.83 | 4.2 | 8.41 | 102.9646 | YES
10 | 1.33 | 149 | 198.17 | 3.2 | 8.46 | 108.0212 | YES
11 | 1.24 | 149 | 184.76 | 3.5 | 8.5 | 106.2116 | YES
12 | 1.15 | 149 | 171.35 | 3.3 | 8.39 | 102.268 | YES
13 | 1.12 | 149 | 166.88 | 3.3 | 8.37 | 101.1442 | YES
14 | 1.8 | 149 | 268.2 | 3.4 | 8.5 | 114.4068 | YES
15 | 1.66 | 149 | 247.34 | 3.8 | 8.66 | 116.1322 | YES
16 | 1.46 | 149 | 217.54 | 4.9 | 8.81 | 111.0002 | YES
17 | 1.23 | 149 | 183.27 | 4.6 | 8.51 | 98.592 | YES
18 | 1.28 | 149 | 190.72 | 6 | 8.86 | 102.4623 | YES
19 | 1.31 | 149 | 195.19 | 5.4 | 8.72 | 101.7859 | YES
20 | 1.2 | 149 | 178.8 | 7.2 | 8.69 | 87.6276 | YES
21 | 1.14 | 149 | 169.86 | 7.6 | 8.03 | 66.4212 | YES
22 | 1.62 | 149 | 241.38 | 7.7 | 8.5 | 82.9357 | YES
23 | 1.62 | 149 | 241.38 | 8.5 | 8.53 | 79.3428 | YES
24 | 0.97 | 149 | 144.53 | 8.4 | 8.32 | 68.5177 | YES
25 | 0.65 | 149 | 96.85 | 10.2 | 8.02 | 52.4277 | YES
26 | 1.4 | 149 | 208.6 | 10.1 | 8.48 | 67.9985 | YES
27 | 1.47 | 149 | 219.03 | 8.5 | 8.45 | 75.6892 | YES
28 | 1.47 | 149 | 219.03 | 7.9 | 8.29 | 74.3837 | YES
29 |  | 149
30 |  | 149
31 |  | 149
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2