## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | CLATSOP
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-03-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.18 |  |  |  | 0.18
2 |  |  | 0.32 |  |  |  | 0.32
3 |  |  | 0.27 |  |  |  | 0.27
4 |  |  | 0.19 |  |  |  | 0.19
5 |  |  | 0.49 |  |  |  | 0.49
6 |  |  | 0.21 |  |  |  | 0.21
7 |  |  | 0.17 |  |  |  | 0.17
8 |  |  | 0.22 |  |  |  | 0.22
9 | [6 empty] | equipment failed
10 |  |  | 0.27 |  |  |  | 0.27
11 |  |  | 0.18 |  |  |  | 0.18
12 |  |  | 0.32 |  |  |  | 0.32
13 |  |  | 0.17 |  |  |  | 0.17
14 |  |  | 0.17 |  |  |  | 0.17
15 |  |  | 0.24 |  |  |  | 0.24
16 |  |  | 0.17 |  |  |  | 0.17
17 |  |  | 0.23 |  |  |  | 0.23
18 |  |  | 0.3 |  |  |  | 0.3
19 |  |  | 0.24 |  |  |  | 0.24
20 |  |  | 0.18 |  |  |  | 0.18
21 |  |  | 0.11 |  |  |  | 0.11
22 |  |  | 0.32 |  |  |  | 0.32
23 |  |  | 0.18 |  |  |  | 0.18
24 |  |  | 0.28 |  |  |  | 0.28
25 |  |  | 0.19 |  |  |  | 0.19
26 |  |  | 0.19 |  |  |  | 0.19
27 |  |  | 0.14 |  |  |  | 0.14
28 |  |  | 0.23 |  |  |  | 0.23
29 |  |  | 0.16 |  |  |  | 0.16
30 |  |  | 0.43 |  |  |  | 0.43
31 |  |  | 0.1 |  |  |  | 0.1
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE: 04/09/2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-03-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.51 | 149 | 224.99 |  | 8.26 | 128.278 | YES
2 | 1.08 | 149 | 160.92 | 9.2 | 8.36 | 66.6748 | YES
3 | 1.03 | 149 | 153.47 | 9.1 | 8.34 | 66.256 | YES
4 | 1.63 | 149 | 242.87 | 8 | 8.34 | 76.6755 | YES
5 | 1.67 | 149 | 248.83 | 7.3 | 8.35 | 81.154 | YES
6 | 1.57 | 149 | 233.93 | 6.5 | 8.02 | 75.0653 | YES
7 | 1.66 | 149 | 247.34 | 7.6 | 8.13 | 73.2296 | YES
8 | 1.58 | 149 | 235.42 | 8.7 | 7.86 | 60.988 | YES
9 | 1.58 | 149 | 235.42 | 8.5 | 7.93 | 63.4121 | YES
10 | 1.37 | 149 | 204.13 | 9.5 | 8.22 | 64.22 | YES
11 | 1.33 | 149 | 198.17 | 7.8 | 8.13 | 69.482 | YES
12 | 1.56 | 149 | 232.44 | 8 | 8.14 | 70.6697 | YES
13 | 1.65 | 149 | 245.85 | 7.5 | 8.18 | 75.0115 | YES
14 | 1.43 | 149 | 213.07 | 8.1 | 8.12 | 68.6207 | YES | 65
15 | 1.25 | 149 | 186.25 | 8.1 | 7.99 | 64.084 | YES | 77
16 | 0.94 | 149 | 140.06 | 8.1 | 7.81 | 57.9161 | YES
17 | 0.95 | 149 | 141.55 | 8.4 | 7.91 | 58.9047 | YES | 83
18 | 1.34 | 149 | 199.66 | 6.8 | 7.85 | 67.2588 | YES | 83
19 | 1.28 | 149 | 190.72 | 7.8 | 7.94 | 64.4562 | YES | 87
20 | 1.22 | 149 | 181.78 | 7.5 | 7.95 | 65.5677 | YES | 87
21 | 1.13 | 149 | 168.37 | 8.3 | 8.1 | 64.8786 | YES | 113
22 | 1.13 | 149 | 168.37 | 7.9 | 8.12 | 67.1631 | YES | 133
23 | 1.09 | 149 | 162.41 | 9 | 8.2 | 63.8445 | YES | 104
24 | 1.19 | 149 | 177.31 | 9.5 | 8.21 | 62.6578 | YES
25 | 1.1 | 149 | 163.9 | 10.4 | 8.14 | 56.8779 | YES | 107
26 | 1.01 | 149 | 150.49 | 11.1 | 8.23 | 55.4583 | YES | 88
27 | 0.92 | 149 | 137.08 | 10.3 | 8.19 | 57.1021 | YES | 93
28 | 1.09 | 149 | 162.41 | 10.4 | 8.09 | 55.7995 | YES | 86
29 | 1.15 | 149 | 171.35 | 11.2 | 8.28 | 56.9997 | YES | 121
30 | 1.15 | 149 | 171.35 | 10.5 | 8.32 | 60.6366 | YES
31 | 1.27 | 149 | 189.23 | 10.2 | 8.37 | 63.9059 | YES
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2