## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | CLATSOP
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-04-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.6 |  |  |  | 0.6 | 0.6
2 |  |  | 0.22 |  |  |  | 0.22 | 0.22
3 |  |  | 0.4 |  |  |  | 0.4 | 0.4
4 |  |  | 0.37 |  |  |  | 0.37 | 0.37
5 |  |  | 0.3 |  |  |  | 0.3 | 0.3
6 |  |  | 0.4 |  |  |  | 0.4 | 0.4
7 |  |  | 0.41 |  |  |  | 0.41 | 0.41
8 |  |  | 0.38 |  |  |  | 0.38 | 0.38
9 |  |  | 0.23 |  |  |  | 0.23 | 0.23
10 |  |  | 0.25 |  |  |  | 0.25 | 0.25
11 |  |  | 0.29 |  |  |  | 0.29 | 0.29
12 |  |  | 0.23 |  |  |  | 0.23 | 0.23
13 |  |  | 0.13 |  |  |  | 0.13 | 0.13
14 |  |  | 0.14 |  |  |  | 0.14 | 0.14
15 |  |  | 0.35 |  |  |  | 0.35 | 0.35
16 |  |  | 0.13 |  |  |  | 0.13 | 0.13
17 |  |  | 0.29 |  |  |  | 0.29 | 0.29
18 |  |  | 0.31 |  |  |  | 0.31 | 0.31
19 |  |  | 0.41 |  |  |  | 0.41 | 0.41
20 |  |  | 0.44 |  |  |  | 0.44 | 0.44
21 |  |  | 0.24 |  |  |  | 0.24 | 0.24
22 |  |  | 0.22 |  |  |  | 0.22 | 0.22
23 |  |  | 0.2 |  |  |  | 0.2 | 0.2
24 |  |  | 0.15 |  |  |  | 0.15 | 0.15
25 |  |  | 0.22 |  |  |  | 0.22 | 0.22
26 |  |  | 0.22 |  |  |  | 0.22 | 0.22
27 |  |  | 0.44 |  |  |  | 0.44 | 0.44
28 |  |  | 0.29 |  |  |  | 0.29 | 0.29
29 |  |  | 0.15 |  |  |  | 0.15 | 0.15
30 |  |  | 0.18 |  |  |  | 0.18 | 0.18
31
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE: 05/09/2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-04-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.74 | 149 | 110.26 | 10.7 | 8.36 | 57.8705 | YES
2 | 1.2 | 149 | 178.8 | 9.5 | 8.29 | 64.5798 | YES | 76
3 | 1.17 | 149 | 174.33 | 8.5 | 8.61 | 77.4789 | YES | 106
4 | 1.57 | 149 | 233.93 | 7.6 | 8.56 | 84.8788 | YES | 116
5 | 1.16 | 149 | 172.84 | 10.7 | 8.29 | 59.243 | YES
6 | 0.76 | 149 | 113.24 | 10.9 | 8.47 | 59.542 | YES
7 | 0.73 | 149 | 108.77 | 10.9 | 8.39 | 57.6468 | YES | 104
8 | 1.22 | 149 | 181.78 | 10.2 | 8.28 | 61.4941 | YES | 110
9 | 1.02 | 149 | 151.98 | 11.1 | 8.07 | 52.4277 | YES | 117
10 | 0.67 | 149 | 99.83 | 10.3 | 8.14 | 54.4887 | YES | 104
11 | 0.57 | 149 | 84.93 | 9.3 | 7.86 | 52.1136 | YES
12 | 0.57 | 149 | 84.93 | 10.8 | 8.02 | 49.9036 | YES
13 | 0.57 | 149 | 84.93 | 10.9 | 8.11 | 51.1867 | YES
14 | 0.58 | 149 | 86.42 | 10.1 | 8.24 | 56.6573 | YES | 105
15 | 1.09 | 149 | 162.41 | 10.6 | 8.25 | 58.3153 | YES | 111
16 | 1.07 | 149 | 159.43 | 10.74 | 8.3 | 58.6805 | YES | 95
17 | 0.96 | 149 | 143.04 | 10.2 | 8.07 | 55.3156 | YES | 91
18 | 0.84 | 149 | 125.16 | 10.8 | 7.45 | 42.078 | YES | 94
19 | 0.95 | 149 | 141.55 | 11.9 | 7.85 | 45.6022 | YES | 100
20 | 1.24 | 149 | 184.76 | 11.4 | 7.98 | 51.0311 | YES | 114
21 | 1.18 | 149 | 175.82 | 10.6 | 8.03 | 54.4415 | YES | 113
22 | 1.04 | 149 | 154.96 | 10 | 8.01 | 55.3799 | YES | 94
23 | 1.22 | 149 | 181.78 | 9.9 | 7.89 | 54.5239 | YES
24 | 0.87 | 149 | 129.63 | 10.4 | 7.9 | 50.827 | YES | 101
25 | 0.95 | 149 | 141.55 | 11.5 | 8.15 | 52.0997 | YES | 94
26 | 1.09 | 149 | 162.41 | 13 | 7.74 | 41.3345 | YES
27 | 0.93 | 149 | 138.57 | 12.2 | 8.34 | 53.0817 | YES
28 | 0.86 | 149 | 128.14 | 12 | 8.11 | 49.1635 | YES
29 | 0.81 | 149 | 120.69 | 11.9 | 7.98 | 46.993 | YES | 99
30 | 1.1 | 149 | 163.9 | 11.3 | 8.16 | 53.9157 | YES | 109
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2