## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | CLATSOP
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-05-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.21 |  |  | 0.21
2 |  |  |  | 0.26 |  |  | 0.26
3 |  |  |  | 0.37 |  |  | 0.37
4 |  |  |  | 0.29 |  |  | 0.29
5 |  |  |  | 0.29 |  |  | 0.29
6 |  |  |  | 0.37 |  |  | 0.37
7 |  |  |  | 0.22 |  |  | 0.22
8 |  |  |  | 0.32 |  |  | 0.32
9 |  |  |  | 0.29 |  |  | 0.29
10 |  |  |  | 0.21 |  |  | 0.21
11 |  |  |  | 0.18 |  |  | 0.18
12 |  |  |  | 0.2 |  |  | 0.2
13 |  |  |  | 0.18 |  |  | 0.18
14 |  |  |  | 0.19 |  |  | 0.19
15 |  |  |  | 0.25 |  |  | 0.25
16 |  |  |  | 0.23 |  |  | 0.23
17 |  |  |  | 0.21 |  |  | 0.21
18 |  |  |  | 0.31 |  |  | 0.31
19 |  |  |  | 0.27 |  |  | 0.27
20 |  |  |  | 0.25 |  |  | 0.25
21 |  |  |  | 0.28 |  |  | 0.28
22 |  |  |  | 0.31 |  |  | 0.31
23 |  |  |  | 0.36 |  |  | 0.36
24 |  |  |  | 0.3 |  |  | 0.3
25 |  |  |  | 0.47 |  |  | 0.47
26 |  |  |  | 0.19 |  |  | 0.19
27 |  |  |  | 0.2 |  |  | 0.2
28 |  |  |  | 0.18 |  |  | 0.18
29 |  |  |  | 0.72 |  |  | 0.72
30 |  |  |  | 0.18 |  |  | 0.18
31 |  |  |  | 0.15 |  |  | 0.15
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE 6-6-2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-05-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.35 | 149 | 201.15 | 11.3 | 7.95 | 51.4721 | YES | 104
2 | 1.14 | 149 | 169.86 | 11.9 | 7.93 | 47.9353 | YES | 124
3 | 1.18 | 149 | 175.82 | 13 | 7.71 | 41.2991 | YES
4 | 1.08 | 149 | 160.92 | 12.8 | 8.03 | 46.5464 | YES
5 | 1 | 149 | 149 | 12.1 | 7.97 | 47.2185 | YES
6 | 0.76 | 149 | 113.24 | 12.5 | 8.36 | 51.6906 | YES
7 | 0.69 | 149 | 102.81 | 13.6 | 8.04 | 42.3973 | YES | 100
8 | 1.5 | 149 | 223.5 | 11.6 | 8.28 | 57.773 | YES | 120
9 | 1.49 | 149 | 222.01 | 12.5 | 8.35 | 55.9172 | YES | 129
10 | 1.19 | 149 | 177.31 | 12.4 | 8.38 | 54.7436 | YES | 119
11 | 1.13 | 149 | 168.37 | 12.1 | 8.24 | 52.7604 | YES | 118
12 | 1 | 149 | 149 | 11.9 | 8.12 | 50.4711 | YES | 103
13 | 0.84 | 149 | 125.16 | 12.6 | 8.17 | 48.3267 | YES | 105
14 | 1 | 149 | 149 | 12.1 | 8.14 | 50.1568 | YES | 103
15 | 1.04 | 149 | 154.96 | 11.6 | 8.15 | 52.2891 | YES | 106
16 | 1.24 | 149 | 184.76 | 12.3 | 8.25 | 52.9081 | YES | 141
17 | 1.44 | 149 | 214.56 | 13.4 | 8.26 | 50.6962 | YES | 110
18 | 1.23 | 149 | 183.27 | 11.7 | 8.24 | 54.8265 | YES | 105
19 | 0.97 | 149 | 144.53 | 12.4 | 8.29 | 51.6832 | YES | 106
20 | 1.28 | 149 | 190.72 | 11.6 | 8.28 | 56.3208 | YES | 112
21 | 1.26 | 149 | 187.74 | 12.1 | 8.41 | 56.9269 | YES | 113
22 | 1.01 | 149 | 150.49 | 12.8 | 8.17 | 48.616 | YES | 125
23 | 0.98 | 149 | 146.02 | 13.1 | 7.88 | 42.6978 | YES | 107
24 | 1.02 | 149 | 151.98 | 13.9 | 7.82 | 39.7876 | YES | 104
25 | 0.63 | 149 | 93.87 | 14.2 | 8.09 | 41.2205 | YES | 100
26 | 0.95 | 149 | 141.55 | 13.7 | 8.2 | 46.002 | YES | 128
27 | 0.99 | 149 | 147.51 | 13.8 | 8.27 | 47.1014 | YES | 140
28 | 1.03 | 149 | 153.47 | 14.1 | 8.29 | 46.7272 | YES | 135
29 | 0.65 | 149 | 96.85 | 14.6 | 8.81 | 52.417 | YES
30 | 0.74 | 149 | 110.26 | 13.3 | 8.13 | 44.9567 | YES | 113
31 | 0.6 | 149 | 89.4 | 15.1 | 8.17 | 39.8579 | YES
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2