## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | CLATSOP
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-06-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  |  | 0.56 |  |  | 0.56
2 |  |  |  | 0.15 |  |  | 0.15
3 |  |  |  | 0.26 |  |  | 0.26
4 |  |  |  | 0.29 |  |  | 0.29
5 |  |  |  | 0.11 |  |  | 0.11
6 |  |  |  | 0.12 |  |  | 0.12
7 |  |  |  | 0.28 |  |  | 0.28
8 |  |  |  | 0.36 |  |  | 0.36
9 |  |  |  | 0.54 |  |  | 0.54
10 |  |  |  | 0.77 |  |  | 0.77
11 |  |  |  | 0.47 |  |  | 0.47
12 |  |  |  | 0.4 |  |  | 0.4
13 |  |  |  | 0.22 |  |  | 0.22
14 |  |  |  | 0.44 |  |  | 0.44
15 |  |  |  | 0.24 |  |  | 0.24
16 |  |  |  | 0.26 |  |  | 0.26
17 |  |  |  | 0.33 |  |  | 0.33
18 |  |  |  | 0.54 |  |  | 0.54
19 |  |  |  | 1.26 |  |  | 1.26
20 |  |  |  | 0.21 |  |  | 0.21
21 |  |  |  | 0.33 |  |  | 0.33
22 |  |  |  | 0.12 |  |  | 0.12
23 |  |  |  | 0.15 |  |  | 0.15
24 |  |  |  | 0.63 |  |  | 0.63
25 |  |  |  | 0.28 |  |  | 0.28
26 |  |  |  | 0.31 |  |  | 0.31
27 |  |  |  | 0.15 |  |  | 0.15
28 |  |  |  | 0.54 |  |  | 0.54
29 |  |  |  | 0.19 |  |  | 0.19
30 |  |  |  | 0.27 |  |  | 0.27
31
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES |  | YES
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE: 07/09/2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-06-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.93 | 149 | 138.57 | 14 | 8.21 | 45.1618 | YES
2 | 1.03 | 149 | 153.47 | 13 | 8.03 | 45.6759 | YES | 99
3 | 0.87 | 149 | 129.63 | 13.2 | 8.21 | 47.2944 | YES | 90
4 | 0.85 | 149 | 126.65 | 13.6 | 7.93 | 41.4591 | YES | 89
5 | 0.86 | 149 | 128.14 | 12.9 | 7.93 | 43.4762 | YES | 91
6 | 1.1 | 149 | 163.9 | 13.7 | 8.07 | 44.6056 | YES | 109
7 | 1.4 | 149 | 208.6 | 13.9 | 8.03 | 44.8726 | YES | 130
8 | 1.25 | 149 | 186.25 | 14.9 | 8.13 | 42.8381 | YES | 111
9 | 1.41 | 149 | 210.09 | 18.6 | 8.23 | 35.4056 | YES
10 | 1.28 | 149 | 190.72 | 17.5 | 8.25 | 37.8108 | YES
11 | 1.06 | 149 | 157.94 | 15.8 | 8.15 | 39.7905 | YES
12 | 1.11 | 149 | 165.39 | 14.7 | 8.09 | 42.1031 | YES | 90
13 | 1.49 | 149 | 222.01 | 14 | 8.24 | 48.6432 | YES | 98
14 | 1.24 | 149 | 184.76 | 13.9 | 8.24 | 47.6033 | YES | 97
15 | 0.98 | 149 | 146.02 | 16.9 | 8.04 | 35.1954 | YES | 140
16 | 0.93 | 149 | 138.57 | 16.2 | 7.85 | 34.1787 | YES | 114
17 | 1.12 | 149 | 166.88 | 13.1 | 7.93 | 44.1842 | YES | 97
18 | 1.31 | 149 | 195.19 | 15.1 | 8.1 | 42.095 | YES
19 | 1.13 | 149 | 168.37 | 14 | 7.83 | 40.1678 | YES
20 | 1.1 | 149 | 163.9 | 13.7 | 7.92 | 42.2114 | YES | 90
21 | 1.12 | 149 | 166.88 | 13.6 | 7.84 | 41.3527 | YES | 84
22 | 1.11 | 149 | 165.39 | 13.8 | 7.93 | 42.1349 | YES | 107
23 | 0.9 | 149 | 134.1 | 13.7 | 7.96 | 41.8788 | YES | 87
24 | 1.3 | 149 | 193.7 | 15 | 8.28 | 45.2234 | YES | 46
25 | 0.61 | 149 | 90.89 | 14.3 | 7.93 | 38.5167 | YES | 90
26 | 1.01 | 149 | 150.49 | 14.4 | 8.05 | 41.8447 | YES | 104
27 | 1.04 | 149 | 154.96 | 14.2 | 8.06 | 42.7039 | YES | 92
28 | 1.18 | 149 | 175.82 | 15.3 | 8.08 | 40.6336 | YES
29 | 1.13 | 149 | 168.37 | 15.7 | 8.13 | 40.0778 | YES | 107
30 | 0.99 | 149 | 147.51 | 15.5 | 8.39 | 43.988 | YES | 95
31 |  | 149
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2