## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | CLATSOP
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-07-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.34 |  |  |  | 0.34
2 |  |  | 0.23 |  |  |  | 0.23
3 |  |  | 0.25 |  |  |  | 0.25
4 |  |  | 0.32 |  |  |  | 0.32
5 |  |  | 0.35 |  |  |  | 0.35
6 |  |  | 0.35 |  |  |  | 0.35
7 |  |  | 0.16 |  |  |  | 0.16
8 |  |  | 0.56 |  |  |  | 0.56
9 |  |  | 0.55 |  |  |  | 0.55
10 |  |  | 0.56 |  |  |  | 0.56
11 |  |  | 0.48 |  |  |  | 0.48
12 |  |  | 0.28 |  |  |  | 0.28
13 |  |  | 0.28 |  |  |  | 0.28
14 |  |  | 0.31 |  |  |  | 0.31
15 |  |  | 0.38 |  |  |  | 0.28
16 |  |  | 0.36 |  |  |  | 0.36
17 |  |  | 0.23 |  |  |  | 0.23
18 |  |  | 0.24 |  |  |  | 0.24
19 |  |  | 0.28 |  |  |  | 0.28
20 |  |  | 0.22 |  |  |  | 0.22
21 |  |  | 0.55 |  |  |  | 0.55
22 |  |  | 0.46 |  |  |  | 0.46
23 |  |  | 0.36 |  |  |  | 0.36
24 |  |  | 0.38 |  |  |  | 0.38
25 |  |  | 0.38 |  |  |  | 0.38
26 |  |  | 0.29 |  |  |  | 0.29
27 |  |  | 0.23 |  |  |  | 0.23
28 |  |  | 0.45 |  |  |  | 0.45
29 |  |  | 0.1 |  |  |  | 0.1
30 |  |  | 0.27 |  |  |  | 0.27
31 |  |  | 0.31 |  |  |  | 0.31
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | SIGNATURE: |  |  | DATE: 08/08/2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-07-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.01 | 149 | 150.49 | 15.1 | 8.03 | 39.6538 | YES | 98
2 | 0.84 | 149 | 125.16 | 15.4 | 7.97 | 37.2959 | YES | 95
3 | 1.17 | 149 | 174.33 | 15.2 | 7.97 | 39.2351 | YES | 97
4 | 1.14 | 149 | 169.86 | 14.3 | 7.84 | 39.5665 | YES | 100
5 | 0.68 | 149 | 101.32 | 16.5 | 7.78 | 31.7307 | YES
6 | 0.64 | 149 | 95.36 | 14.6 | 7.71 | 34.931 | YES
7 | 0.53 | 149 | 78.97 | 15.1 | 7.82 | 34.7527 | YES | 106
8 | 0.65 | 149 | 96.85 | 14.8 | 7.58 | 32.889 | YES
9 | 1.04 | 149 | 154.96 | 15.9 | 7.68 | 33.156 | YES
10 | 0.59 | 149 | 87.91 | 18.6 | 7.75 | 26.9929 | YES
11 | 0.55 | 149 | 81.95 | 16 | 7.71 | 31.4972 | YES
12 | 0.74 | 149 | 110.26 | 15.6 | 7.81 | 34.3003 | YES | 126
13 | 0.96 | 149 | 143.04 | 16.1 | 7.78 | 33.6425 | YES | 122
14 | 0.79 | 149 | 117.71 | 16.2 | 7.86 | 33.7637 | YES | 102
15 | 0.71 | 149 | 105.79 | 16 | 7.96 | 35.1828 | YES | 101
16 | 0.73 | 149 | 108.77 | 16.4 | 7.79 | 32.2444 | YES | 126
17 | 1.06 | 149 | 157.94 | 16.4 | 7.98 | 35.9126 | YES | 117
18 | 1.13 | 149 | 168.37 | 16.1 | 7.95 | 36.5214 | YES | 97
19 | 1.02 | 149 | 151.98 | 16.4 | 7.94 | 35.2257 | YES | 103
20 | 0.94 | 149 | 140.06 | 16.4 | 8.01 | 35.8213 | YES | 104
21 | 0.66 | 149 | 98.34 | 16.7 | 8.23 | 36.8933 | YES
22 | 0.41 | 149 | 61.09 | 16.5 | 8.37 | 38.2674 | YES
23 | 0.53 | 149 | 78.97 | 15.6 | 8.05 | 36.5962 | YES
24 | 0.44 | 149 | 65.56 | 16 | 8.32 | 38.9685 | YES
25 | 0.47 | 149 | 70.03 | 15.5 | 7.91 | 34.7467 | YES | 100
26 | 0.57 | 149 | 84.93 | 15.5 | 8.13 | 38.116 | YES | 104
27 | 0.49 | 149 | 73.01 | 15.6 | 7.75 | 32.6074 | YES | 104
28 | 0.64 | 149 | 95.36 | 14.7 | 7.81 | 36.0049 | YES | 107
29 | 0.63 | 149 | 93.87 | 14.8 | 7.98 | 38.0386 | YES | 121
30 | 0.91 | 149 | 135.59 | 15.5 | 8.01 | 37.8994 | YES | 130
31 | 0.96 | 149 | 143.04 | 15.6 | 8.07 | 38.7095 | YES | 121
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2