## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | CLATSOP
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-08-01
System Name: | WICKIUP WATER DISTRICT |  |  | ID#: 41 | 00063 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0.21 |  |  |  | 0.21
2 |  |  | 0.39 |  |  |  | 0.39
3 |  |  | 0.42 |  |  |  | 0.42
4 |  |  | 0.24 |  |  |  | 0.24
5 |  |  | 0.17 |  |  |  | 0.17
6 |  |  | 0.14 |  |  |  | 0.14
7 |  |  | 0.28 |  |  |  | 0.28
8 |  |  | 0.24 |  |  |  | 0.24
9 |  |  | 0.45 |  |  |  | 0.45
10 |  |  | 0.59 |  |  |  | 0.59
11 |  |  | 0.34 |  |  |  | 0.34
12 |  |  | 0.23 |  |  |  | 0.23
13 |  |  | 0.47 |  |  |  | 0.47
14 |  |  | 0.6 |  |  |  | 0.6
15 |  |  | 0.67 |  |  |  | 0.67
16 |  |  | 0.32 |  |  |  | 0.32
17 |  |  | 0.25 |  |  |  | 0.25
18 |  |  | 0.25 |  |  |  | 0.25
19 |  |  | 0.16 |  |  |  | 0.16
20 |  |  | 0.14 |  |  |  | 0.14
21 |  |  | 0.16 |  |  |  | 0.16
22 |  |  | 0.19 |  |  |  | 0.19
23 |  |  | 0.59 |  |  |  | 0.59
24 |  |  | 0.28 |  |  |  | 0.28
25 |  |  | 0.29 |  |  |  | 0.29
26 |  |  | 0.7 |  |  |  | 0.7
27 |  |  | 0.54 |  |  |  | 0.54
28 |  |  | 0.62 |  |  |  | 0.62
29 |  |  | 0.23 |  |  |  | 0.23
30 |  |  | 0.25 |  |  |  | 0.25
31 |  |  | 0.19 |  |  |  | 0.19
Slow Sand/Membrane/DE Filtration/Unfiltered
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: ERIC BUFKIN
[5 empty] | #VALUE! |  |  | DATE: 09/08/2025
[5 empty] | PHONE #: (503) 468-8998 |  |  | CERT #: T-08793
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | A
System Name: | WICKIUP WATER DISTRICT |  | ID#: 41 | 00063 | Month/Year: | 2025-08-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.92 | 149 | 137.08 | 16 | 7.94 | 35.7667 | YES | 84
2 | 0.66 | 149 | 98.34 | 16.7 | 7.89 | 32.5376 | YES
3 | 0.77 | 149 | 114.73 | 16.1 | 7.92 | 34.6724 | YES
4 | 0.65 | 149 | 96.85 | 15.6 | 8.04 | 36.9612 | YES | 107
5 | 0.91 | 149 | 135.59 | 16.5 | 7.78 | 32.5723 | YES | 86
6 | 0.71 | 149 | 105.79 | 16.3 | 8.13 | 36.7221 | YES | 94
7 | 0.53 | 149 | 78.97 | 15.8 | 7.83 | 33.2935 | YES
8 | 0.53 | 149 | 78.97 | 17.3 | 7.92 | 31.1466 | YES
9 | 0.8 | 149 | 119.2 | 19.5 | 7.9 | 27.5252 | YES
10 | 0.84 | 149 | 125.16 | 17.4 | 8.02 | 33.2594 | YES
11 | 1.06 | 149 | 157.94 | 18.7 | 8 | 31.0416 | YES | 120
12 | 0.85 | 149 | 126.65 | 17.5 | 7.95 | 32.2305 | YES | 122
13 | 1.15 | 149 | 171.35 | 17.5 | 7.95 | 33.3495 | YES | 111
14 | 1.02 | 149 | 151.98 | 17.5 | 8.03 | 33.8468 | YES | 101
15 | 0.88 | 149 | 131.12 | 17.4 | 7.98 | 32.9204 | YES
16 | 0.8 | 149 | 119.2 | 18 | 8.2 | 34.0014 | YES
17 | 0.52 | 149 | 77.48 | 17.8 | 7.99 | 30.8811 | YES
18 | 0.42 | 149 | 62.58 | 17.6 | 7.88 | 29.705 | YES
19 | 0.82 | 149 | 122.18 | 17.7 | 7.91 | 31.2291 | YES | 86
20 | 0.73 | 149 | 108.77 | 16.8 | 8.04 | 34.4383 | YES | 104
21 | 0.61 | 149 | 90.89 | 15.4 | 8 | 36.7398 | YES | 104
22 | 0.61 | 149 | 90.89 | 15.7 | 8.01 | 36.1477 | YES
23 | 0.83 | 149 | 123.67 | 16.6 | 7.44 | 28.265 | YES
24 | 0.69 | 149 | 102.81 | 16.9 | 8.08 | 34.5619 | YES
25 | 0.7 | 149 | 104.3 | 15.8 | 8.01 | 36.2769 | YES
26 | 0.88 | 149 | 131.12 | 17.3 | 8.1 | 34.6437 | YES
27 | 0.68 | 149 | 101.32 | 16.9 | 7.93 | 32.6599 | YES
28 | 0.7 | 149 | 104.3 | 16.7 | 8.13 | 35.7181 | YES
29 | 1.44 | 149 | 214.56 | 16.4 | 8.13 | 39.6267 | YES
30 | 1.37 | 149 | 204.13 | 16.3 | 8.13 | 39.5754 | YES | 101
31 | 0.97 | 149 | 144.53 | 16 | 8.16 | 39.0111 | YES | 104
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2